## Function In Use
Tag | Old Tag | Description | XMG - Misalignment Guard | XOS - Overflow Switch | XRG - Rotation Guard | XFS - Flow Switch | XEX - Explosion Signal | XDWN - Downstream Signal | XTT - Temperature | XDS - Door Switch | XPF - Power Fault | XSS - Safety System | XIS - Isolator Fault | XMCB - Circuit Breaker Fault | XTH - Thermistor | XLS - Level Switch | XINT1 - Undefined | XINT2 - Undefined | XINT3 - Undefined | XINT4 - Undefined | XINT5 - Undefined | XINT6 - Undefined | XINT7 - Undefined | XINT8 - Undefined | External Block Comments | XDWN | PF Comments | MCB Comments | XINT1 Comment | XINT2 Comment | XINT3 Comment | Rev | Rev Comments
C8010_FA01_MO01 | VE13 | Bulk Intake Pit Extract Fan 1-Motor | [11 empty] | 1
C8010_FI01_DO01 | FI13 | Bulk Intake Pit Filter 1-Start Command
C8010_FA02_MO01 | VE14 | Bulk Intake Pit Extract Fan 2-Motor | [11 empty] | 1
C8010_FI02_DO01 | FI14 | Bulk Intake Pit Filter 2-Start Command
C8010_FA03_MO01 | VE15 | Bulk Intake Pit Extract Fan 3-Motor | [11 empty] | 1
C8010_FI03_DO01 | FI15 | Bulk Intake Pit Filter 3-Start Command
C8010_SCW01_MO01 | T01 | Bulk Intake Screw Conveyor 1-Motor |  | 1 |  |  |  | 1 | [5 empty] | 1 | [11 empty] | C8010_EV01_MO01
C8010_EV01_MO01 | E01 | Bulk Intake Elevator 1-Start | 1 |  | 1 |  |  | 1 | [5 empty] | 1 | [10 empty] | 4 MGs | C8010_SCW02_MO01
C8010_FA04_MO01 | VE18 | Bulk Intake Elevator 1 Fan-Motor | [11 empty] | 1
C8010_SCW02_MO01 | T02 | Bulk Intake Screw Conveyor 2-Motor |  | 1 |  |  |  | 1 | [5 empty] | 1 | [11 empty] | C8010_EV02_MO01
C8010_EV02_MO01 | E02 | Bulk Intake Elevator 2-Start | 1 |  | 1 |  |  | 1 | [5 empty] | 1 | [10 empty] | 4 MGs | C8020_SCW01_MO01 OR C8020_CN01_MO01 depending on position of C8020_DV01
C8010_FA05_MO01 | VE19 | Bulk Intake Elevator 2 Fan-Motor | [11 empty] | 1
C8020_SCW01_MO01 | T03 | Silo Top Screw Conveyor 1-Motor |  | 1 |  |  |  | 1 | [5 empty] | 1 | [11 empty] | C8020_SCW02_MO01
C8020_FA01_MO01 | VE20 | Silo Top Screw Conveyor 1 Fan-Motor | [11 empty] | 1
C8020_FI01_DO01 | FI20 | Silo Top Conveyor 1 Filter-Start Command
C8020_SCW02_MO01 | T04 | Silo Top Screw Conveyor 2-Motor |  | 1 |  |  |  | 1 | [5 empty] | 1 | [10 empty] | 2 Overflow Switches, one at each end | C8020_DP01_FB02 OR C8020_DP02_FB02 telescopic pipe extended AND C8020_SG0X_FB02 (X=Destination Silo)
C8020_FA02_MO01 | VE21 | Silo Top Screw Conveyor 2 Fan-Motor | [11 empty] | 1
C8020_FI02_DO01 | FI21 | Silo Top Conveyor 2 Filter-Start Command
C8020_DB01_MO01 | RT04 | Silo Top Rotating Distributor-Motor | [11 empty] | 1 |  |  | 1 | 1 | [10 empty] | Endstop Right | Endstop Left
C8020_FI03_DO01 | FI33 | Bulk Silo 1 Filter-Start Command
C8020_FI04_DO01 | FI34 | Bulk Silo 4 Filter-Start Command
C8020_FA09_MO01 | VE31 | Bulk Silo 13 Fan-Motor | [11 empty] | 1
C8020_FI09_DO01 | FI31 | Bulk Silo 13 Filter-Start Command
C8020_FA07_MO01 | VE42 | Bulk Silo 15 Fan-Motor | [11 empty] | 1
C8020_FI07_DO01 | FI42 | Bulk Silo 15 Filter-Start Command
C8020_FA08_MO01 | VE41 | Bulk Silo 16 Fan-Motor | [11 empty] | 1
C8020_FI08_DO01 | FI41 | Bulk Silo 16 Filter-Start Command
C8020_FA10_MO01 | VE16 | Bulk Silo 23-25 Fan 1-Motor | [11 empty] | 1
C8020_FA11_MO01 | VE17 | Bulk Silo 23-25 Fan 2-Motor | [11 empty] | 1
C8020_CN01_MO01 | T65 | Silo Top Chain Conveyor 1-Motor |  | 1 |  |  |  | 1 | [5 empty] | 1 | [11 empty] | C8020_BV07_FB02 OR C8020_BV08_FB02 depending on position of C8020_DV02 | [5 empty] | V1.2 | Removed XFS
C8020_FI05_DO01 | FI35 | Bulk Silo 7 Filter-Start Command
C8020_FI06_DO01 | FI36 | Bulk Silo 8 Filter-Start Command
C8040_FA01_MO01 | VE20 | Micro Dosing Room Extract Fan-Motor | [11 empty] | 1
C8040_FI01_DO01 | FI20 | Micro Dosing Filter-Start Command
C8040_LF01_MO01 | HOIST | Hoist at Top of Micro Silos-Motor Up/Down | [9 empty] | 1 | 1 | 1 | [10 empty] | 3 emergency stop signals | [6 empty] | V1.2 | 3 Emergency Stop circuits added
C8040_LF01_MO02 | HOIST | Hoist at Top of Micro Silos-Motor Left/Right | [9 empty] | 1 | 1 | 1 | [10 empty] | 3 emergency stop signals | [6 empty] | V1.2 | 3 Emergency Stop circuits added
C8040_LF01_MO03 | HOIST | Hoist at Top of Micro Silos-Motor Forward/Back | [9 empty] | 1 | 1 | 1 | [10 empty] | 3 emergency stop signals | [6 empty] | V1.2 | 3 Emergency Stop circuits added
C8040_LF01_PB01_DO01 | HOIST | Level 0 Hoist Command-Level 0 Lamp Indication
C8040_LF01_PB02_DO02 | HOIST | Level 2 Hoist Command-Level 2 Lamp Indication
C8110_SCW01_MO01 | EX1 | Dosing Screw Silo 1-Motor | [5 empty] | 1 |  |  | 1 | [5 empty] | 1 | [8 empty] | NOT C8112_CN01_XGH | Tripped Breaker on VSD or VSD Fault |  | Scale Comms |  |  | V1.2 | Modified PF Comments
C8110_SCW02_MO01 | EX2 | Dosing Screw Silo 2-Motor | [5 empty] | 1 |  |  | 1 | [5 empty] | 1 | [8 empty] | NOT C8112_CN01_XGH | Tripped Breaker on VSD or VSD Fault |  | Scale Comms |  |  | V1.2 | Modified PF Comments
C8110_SCW03_MO01 | EX3 | Dosing Screw Silo 3-Motor | [5 empty] | 1 |  |  | 1 | [5 empty] | 1 | [8 empty] | NOT C8112_CN01_XGH | Tripped Breaker on VSD or VSD Fault |  | Scale Comms |  |  | V1.2 | Modified PF Comments
C8110_SCW04_MO01 | EX4 | Dosing Screw Silo 4-Motor | [5 empty] | 1 |  |  | 1 | [5 empty] | 1 | [8 empty] | NOT C8112_CN01_XGH | Tripped Breaker on VSD or VSD Fault |  | Scale Comms |  |  | V1.2 | Modified PF Comments
C8110_SCW05_MO01 | EX5 | Dosing Screw Silo 5-Motor | [5 empty] | 1 |  |  | 1 | [5 empty] | 1 | [8 empty] | NOT C8112_CN01_XGH | Tripped Breaker on VSD or VSD Fault |  | Scale Comms |  |  | V1.2 | Modified PF Comments
C8110_SCW06_MO01 | EX6 | Dosing Screw Silo 6-Motor | [5 empty] | 1 |  |  | 1 | [5 empty] | 1 | [8 empty] | NOT C8112_CN01_XGH | Tripped Breaker on VSD or VSD Fault |  | Scale Comms |  |  | V1.2 | Modified PF Comments
C8110_SCW07_MO01 | EX7 | Dosing Screw Silo 7-Motor | [5 empty] | 1 |  |  | 1 | [5 empty] | 1 | [8 empty] | NOT C8112_CN01_XGH | Tripped Breaker on VSD or VSD Fault |  | Scale Comms |  |  | V1.2 | Modified PF Comments
C8110_SCW08_MO01 | EX8 | Dosing Screw Silo 8-Motor | [5 empty] | 1 |  |  | 1 | [5 empty] | 1 | [8 empty] | NOT C8112_CN01_XGH | Tripped Breaker on VSD or VSD Fault |  | Scale Comms |  |  | V1.2 | Modified PF Comments
C8110_SCW09_MO01 | EX9 | Dosing Screw Silo 9-Motor | [5 empty] | 1 |  |  | 1 | [5 empty] | 1 | [8 empty] | NOT C8112_CN01_XGH | Tripped Breaker on VSD or VSD Fault |  | Scale Comms |  |  | V1.2 | Modified PF Comments
C8110_VB09_MO01 | EX9 | Dosing Vibro Silo 9-Motor
C8110_VB09_MO02 | EX9 | Dosing Vibro Silo 9-Motor | [29 empty] | V1.2 | Modified PF Comments
C8110_SCW10_MO01 | EX10 | Dosing Screw Silo 10-Motor | [5 empty] | 1 |  |  | 1 | [5 empty] | 1 | [8 empty] | NOT C8112_CN01_XGH | Tripped Breaker on VSD or VSD Fault |  | Scale Comms
C8110_VB10_MO01 | EX10 | Dosing Vibro Silo 10-Motor
C8110_VB10_MO02 | EX10 | Dosing Vibro Silo 10-Motor
C8110_SCW13_MO01 | EX13 | Dosing Screw Silo 13-Motor | [5 empty] | 1 |  |  | 1 | [5 empty] | 1 | [8 empty] | NOT C8112_CN01_XGH | Tripped Breaker on VSD or VSD Fault |  | Scale Comms |  |  | V1.2 | Modified PF Comments
C8110_SCW14_MO01 | EX14 | Dosing Screw Silo 14-Motor | [5 empty] | 1 |  |  | 1 | [5 empty] | 1 | [8 empty] | NOT C8112_CN01_XGH | Tripped Breaker on VSD or VSD Fault |  | Scale Comms |  |  | V1.2 | Modified PF Comments
C8110_SCW15_MO01 | EX15 | Dosing Screw Silo 15-Motor | [5 empty] | 1 |  |  | 1 | [5 empty] | 1 | [8 empty] | NOT C8112_CN01_XGH | Tripped Breaker on VSD or VSD Fault |  | Scale Comms |  |  | V1.2 | Modified PF Comments
C8110_SCW16_MO01 | EX16 | Dosing Screw Silo 16-Motor | [5 empty] | 1 |  |  | 1 | [5 empty] | 1 | [8 empty] | NOT C8112_CN01_XGH | Tripped Breaker on VSD or VSD Fault |  | Scale Comms |  |  | V1.2 | Modified PF Comments
C8110_VB16_MO01 | EX16 | Dosing Vibro Silo 16-Motor
C8110_VB16_MO02 | EX16 | Dosing Vibro Silo 16-Motor
C8110_SCW17_MO01 | EX17 | Dosing Screw Silo 17-Motor | [5 empty] | 1 |  |  | 1 | [5 empty] | 1 | [8 empty] | NOT C8112_CN01_XGH | Tripped Breaker on VSD or VSD Fault |  | Scale Comms |  |  | V1.2 | Modified PF Comments
C8110_SCW18_MO01 | EX18 | Dosing Screw Silo 18-Motor | [5 empty] | 1 |  |  | 1 | [5 empty] | 1 | [8 empty] | NOT C8112_CN01_XGH | Tripped Breaker on VSD or VSD Fault |  | Scale Comms |  |  | V1.2 | Modified PF Comments
C8110_SCW19_MO01 | EX19 | Dosing Screw Silo 19-Motor | [5 empty] | 1 |  |  | 1 | [5 empty] | 1 | [8 empty] | NOT C8112_CN01_XGH | Tripped Breaker on VSD or VSD Fault |  | Scale Comms |  |  | V1.2 | Modified PF Comments
C8110_VB19_MO01 | EX19 | Dosing Vibro Silo 19-Motor
C8110_VB19_MO02 | EX19 | Dosing Vibro Silo 19-Motor
C8110_SCW20_MO01 | EX20 | Dosing Screw Silo 20-Motor | [5 empty] | 1 |  |  | 1 | [5 empty] | 1 | [8 empty] | NOT C8112_CN01_XGH | Tripped Breaker on VSD or VSD Fault |  | Scale Comms |  |  | V1.2 | Modified PF Comments
C8110_SCW23_MO01 | EX23 | Dosing Screw Silo 23-Motor | [5 empty] | 1 |  |  | 1 | [5 empty] | 1 | [8 empty] | NOT C8112_CN01_XGH | Tripped Breaker on VSD or VSD Fault |  | Scale Comms |  |  | V1.2 | Modified PF Comments
C8110_SCW24_MO01 | EX24 | Dosing Screw Silo 24-Motor | [5 empty] | 1 |  |  | 1 | [5 empty] | 1 | [8 empty] | NOT C8112_CN01_XGH | Tripped Breaker on VSD or VSD Fault |  | Scale Comms |  |  | V1.2 | Modified PF Comments
C8110_SCW25_MO01 | EX25 | Dosing Screw Silo 25-Motor | [5 empty] | 1 |  |  | 1 | [5 empty] | 1 | [8 empty] | NOT C8112_CN01_XGH | Tripped Breaker on VSD or VSD Fault |  | Scale Comms |  |  | V1.2 | Modified PF Comments
C8112_CN01_MO01 | T09 | Primary Dosing Scale Discharge Conveyor-Motor |  | 1 |  |  |  | 1 | [17 empty] | C8114_CN01_MO01
C8112_FA01_MO01 | FT09 | Scale Discharge Conveyor Aspiration Fan-Motor
C8114_CN01_MO01 | T10 | Batch Transport Conveyor 1-Motor |  | 1 |  |  |  | 1 | [17 empty] | C8114_EV01_MO01 | [5 empty] | V1.2 | Removed XFS
C8114_FA01_MO01 | FT10 | Batch Transport Conveyor Aspiration Fan-Motor
C8114_EV01_MO01 | E03 | Batch Transport Elevator 1-Start | 1 |  | 1 | [19 empty] | 4 MGs | [6 empty] | V1.2 | Removed XLS
C8114_FA02_MO01 | FE3 | Batch Transport Elevator Aspiration Fan-Motor
C8120_MX01_MO01 | M02 | Pre-Mixer-Motor
C8122_SCW01_MO01 | AL01 | Grinder 1 Feed Screw-Motor |  | 1 |  |  |  | 1 | 1 |  | 1 |  |  | 1 |  | 1 | [9 empty] | C8122_CR01_MO01 |  | From VSD |  |  |  | V1.2 | Added XPF. Added XLS (8124_TA01_LSL01)
C8122_SCW01_MO02 | AL01 | Grinder 1 Feed Screw-Forced Ventilation Motor | [11 empty] | 1
C8122_CR01_MO01 | PB01 | Grinder 1 Lump Crusher-Motor |  |  | 1 |  |  | 1 | 1 |  | 1 |  |  | 1 | [10 empty] | 2 TTs and 2 MCBs | C8122_ML01_MO01 | Soft Starter Fault
C8122_ML01_MO01 | BR01 | Grinder 1-Motor | [5 empty] | 1 | 1 | 1 | 1 | 1 |  | 1 | [10 empty] | 2 TTs and 2 MCBs | C8124_SCW01_MO01
C8122_ML01_SS02_LP01 | KA180 | Grinder 1 Door Safety System-Indication Lamp
C8122_FA01_MO01 | VE03 | Grinder 1 Extract Fan-Motor | [8 empty] | 1 |  |  | 1 | [12 empty] | VSD Fault
C8122_SCW02_MO01 | AL02 | Grinder 2 Feed Screw-Motor |  | 1 |  |  |  | 1 | 1 |  | 1 |  |  | 1 |  | 1 | [9 empty] | C8122_CR02_MO01 |  | From VSD |  |  |  | V1.2 | Added XPF. Added XLS (8124_TA02_LSL01)
C8122_SCW02_MO02 | AL02 | Grinder 1 Feed Screw-Forced Ventilation Motor | [11 empty] | 1
C8122_CR02_MO01 | PB02 | Grinder 2 Lump Crusher-Motor |  |  | 1 |  |  | 1 | 1 |  | 1 |  |  | 1 | [10 empty] | 2 TTs and 2 MCBs | C8122_ML02_MO01 | Soft Starter Fault
C8122_ML02_MO01 | BR02 | Grinder 2-Motor | [5 empty] | 1 | 1 | 1 | 1 | 1 |  | 1 | [10 empty] | 2 TTs and 2 MCBs | C8124_SCW02_MO01
C8122_ML02_SS02_LP01 | KA180 | Grinder 2 Door Safety System-Indication Lamp
C8122_FA02_MO01 | VE04 | Grinder 2 Extract Fan-Motor | [8 empty] | 1 |  |  | 1 | [12 empty] | VSD Fault
C8124_RV01_MO01 | EC02 | Grinder 1 Rotary Valve-Motor
C8124_SCW01_MO01 | T13 | Grinder 1 Discharge Screw-Motor | [5 empty] | 1 | [17 empty] | C8124_RV01_MO01 | [5 empty] | V1.1 | Removed XOS and changed Downstream signal
C8124_RV02_MO01 | EC03 | Grinder 2 Rotary Valve-Motor
C8124_SCW02_MO01 | T14 | Grinder 2 Discharge Screw-Motor | [5 empty] | 1 | [17 empty] | C8124_RV02_MO01 | [5 empty] | V1.1 | Removed XOS
C8130_FA01_MO01 | VE07 | Weigh Bin Extract Fan-Motor
C8130_SCW31_MO01 | EX7 | Dosing Screw Silo 31-Motor | [5 empty] | 1 |  |  | 1 | [5 empty] | 1 | [8 empty] | C8132_SG31_FB02 | Tripped Breaker on VSD or VSD Fault |  | Scale Comms |  |  | V1.2 | Modified XDWN text and PF Comments
C8130_SCW32_MO01 | EX8 | Dosing Screw Silo 32-Motor | [5 empty] | 1 |  |  | 1 | [5 empty] | 1 | [8 empty] | C8132_SG32_FB02 | Tripped Breaker on VSD or VSD Fault |  | Scale Comms |  |  | V1.2 | Modified XDWN text and PF Comments
C8130_SCW33_MO01 | EX9 | Dosing Screw Silo 33-Motor | [5 empty] | 1 |  |  | 1 | [5 empty] | 1 | [8 empty] | C8132_SG33_FB02 | Tripped Breaker on VSD or VSD Fault |  | Scale Comms |  |  | V1.2 | Modified XDWN text and PF Comments
C8130_SCW34_MO01 | EX10 | Dosing Screw Silo 34-Motor | [5 empty] | 1 |  |  | 1 | [5 empty] | 1 | [8 empty] | C8132_SG34_FB02 | Tripped Breaker on VSD or VSD Fault |  | Scale Comms |  |  | V1.2 | Modified XDWN text and PF Comments
C8140_SB55_MO01 | DE55 | Scraper Bottom Silo 55-Motor | [10 empty] | 1 | 1
C8140_SCW55_MO01 | EX55 | Dosing Screw Silo 55-Motor | [5 empty] | 1 |  |  | 1 |  | 1 |  |  |  | 1 | [8 empty] | C8140_FV55_FB02 | Tripped Breaker on VSD or VSD Fault |  | Scale Comms |  |  | V1.2 | Modified PF Comments
C8140_SB56_MO01 | DE56 | Scraper Bottom Silo 56-Motor | [10 empty] | 1 | 1
C8140_SCW56_MO01 | EX56 | Dosing Screw Silo 56-Motor | [5 empty] | 1 |  |  | 1 |  | 1 |  |  |  | 1 | [8 empty] | C8140_FV56_FB02 | Tripped Breaker on VSD or VSD Fault |  | Scale Comms |  |  | V1.2 | Modified PF Comments
C8140_SB57_MO01 | DE57 | Scraper Bottom Silo 57-Motor | [10 empty] | 1 | 1
C8140_SCW57_MO01 | EX57 | Dosing Screw Silo 57-Motor | [5 empty] | 1 |  |  | 1 |  | 1 |  |  |  | 1 | [8 empty] | C8140_FV57_FB02 | Tripped Breaker on VSD or VSD Fault |  | Scale Comms |  |  | V1.2 | Modified PF Comments
C8140_SB58_MO01 | DE58 | Scraper Bottom Silo 58-Motor | [10 empty] | 1 | 1
C8140_SCW58_MO01 | EX58 | Dosing Screw Silo 58-Motor | [5 empty] | 1 |  |  | 1 |  | 1 |  |  |  | 1 | [8 empty] | C8140_FV58_FB02 | Tripped Breaker on VSD or VSD Fault |  | Scale Comms |  |  | V1.2 | Modified PF Comments
C8140_SB59_MO01 | DE59 | Scraper Bottom Silo 59-Motor | [10 empty] | 1 | 1
C8140_SCW59_MO01 | EX59 | Dosing Screw Silo 59-Motor | [5 empty] | 1 |  |  | 1 |  | 1 |  |  |  | 1 | [8 empty] | C8140_FV59_FB02 | Tripped Breaker on VSD or VSD Fault |  | Scale Comms |  |  | V1.2 | Modified PF Comments
C8140_SB60_MO01 | DE60 | Scraper Bottom Silo 60-Motor | [10 empty] | 1 | 1
C8140_SCW60_MO01 | EX60 | Dosing Screw Silo 60-Motor | [5 empty] | 1 |  |  | 1 |  | 1 |  |  |  | 1 | [8 empty] | C8140_FV60_FB02 | Tripped Breaker on VSD or VSD Fault |  | Scale Comms |  |  | V1.2 | Modified PF Comments
C8140_SCW61_MO01 | EX61 | Dosing Screw Silo 61-Motor | [5 empty] | 1 |  |  | 1 |  | 1 |  |  |  | 1 | [8 empty] | C8140_FV61_FB02 | Tripped Breaker on VSD or VSD Fault |  | Scale Comms |  |  | V1.2 | Modified PF Comments
C8140_SCW62_MO01 | EX62 | Dosing Screw Silo 62-Motor | [5 empty] | 1 |  |  | 1 |  | 1 |  |  |  | 1 | [8 empty] | C8140_FV62_FB02 | Tripped Breaker on VSD or VSD Fault |  | Scale Comms |  |  | V1.2 | Modified PF Comments
C8140_SCW63_MO01 | EX63 | Dosing Screw Silo 63-Motor | [5 empty] | 1 |  |  | 1 |  | 1 |  |  |  | 1 | [8 empty] | C8140_FV63_FB02 | Tripped Breaker on VSD or VSD Fault |  | Scale Comms |  |  | V1.2 | Modified PF Comments
C8140_SCW64_MO01 | EX64 | Dosing Screw Silo 64-Motor | [5 empty] | 1 |  |  | 1 |  | 1 |  |  |  | 1 | [8 empty] | C8140_FV64_FB02 | Tripped Breaker on VSD or VSD Fault |  | Scale Comms |  |  | V1.2 | Modified PF Comments
C8140_SCW65_MO01 | EX65 | Dosing Screw Silo 65-Motor | [5 empty] | 1 |  |  | 1 |  | 1 |  |  |  | 1 | [8 empty] | C8140_FV65_FB02 | Tripped Breaker on VSD or VSD Fault |  | Scale Comms |  |  | V1.2 | Modified PF Comments
C8140_SCW66_MO01 | EX66 | Dosing Screw Silo 66-Motor | [5 empty] | 1 |  |  | 1 |  | 1 |  |  |  | 1 | [8 empty] | C8140_FV66_FB02 | Tripped Breaker on VSD or VSD Fault |  | Scale Comms |  |  | V1.2 | Modified PF Comments
C8140_SCW67_MO01 | EX67 | Dosing Screw Silo 67-Motor | [5 empty] | 1 |  |  | 1 |  | 1 |  |  |  | 1 | [8 empty] | C8140_FV67_FB02 | Tripped Breaker on VSD or VSD Fault |  | Scale Comms |  |  | V1.2 | Modified PF Comments
C8140_SCW68_MO01 | EX68 | Dosing Screw Silo 68-Motor | [5 empty] | 1 |  |  | 1 |  | 1 |  |  |  | 1 | [8 empty] | C8140_FV68_FB02 | Tripped Breaker on VSD or VSD Fault |  | Scale Comms |  |  | V1.2 | Modified PF Comments
C8142_HM01_SV02 |  | Hammer on Micro Scale 1-Solenoid Valve
C8142_MX01_MO01 | M08 | Micro Mixer-Motor | [10 empty] | 1 | 1
C8150_FA01_MO01 | VS02 | Main Mixer Aspiration Fan-Motor
C8150_FI01_SV02 | FI25 | Main Mixer Filter-Solenoid Valve
C8150_MX01_MO01 | M03 | Main Mixer-Motor | [6 empty] | 1 | [5 empty] | 1
C8150_CN01_MO01 | T15 | Main Mixer Conveyor-Motor |  | 1 |  |  |  | 1 | [17 empty] | C8152_EV01_MO01
C8152_EV01_MO01 | E05 | Mixer Elevator-Start | 1 |  | 1 | [19 empty] | 4 MGs
C8152_FA01_MO01 | FE5 | Mixer Elevator Aspiration Fan-Motor
C8152_DB01_MO01 | DI04 | Distributor - Extruder Pre-Bins-Motor
C8210_FA01_MO01 | FI51 | Exturder Pre-Bin 1 Aspiration Fan-Motor
C8210_FI01_SV02 | FI51 | Exturder Pre-Bin 1 Filter-Solenoid Valve
C8210_FA02_MO01 | FI52 | Exturder Pre-Bin 2 Aspiration Fan-Motor
C8210_FI02_SV02 | FI52 | Exturder Pre-Bin 2 Filter-Solenoid Valve
C8210_SCW01_MO01 | EX41 | Discharge Screw Extruder Pre-Bin 1-Motor |  | 1 |  |  |  | 1 |  |  | 1 | [14 empty] | C8210_SCW05_MO01 | Tripped Breaker on VSD or VSD Fault |  |  |  |  | V1.2 | Modified PF Comments
C8210_SCW02_MO01 | EX42 | Discharge Screw Extruder Pre-Bin 2-Motor |  | 1 |  |  |  | 1 |  |  | 1 | [14 empty] | C8210_SCW05_MO01 | Tripped Breaker on VSD or VSD Fault |  |  |  |  | V1.2 | Modified PF Comments
C8210_SCW05_MO01 | T08 | Discharge Screw Extruder Pre-Bins-Motor |  | 1 |  |  |  | 1 | [17 empty] | C8210_DV01/02 = Waste OR (C8210_SI01_MO01 AND C8210_SI02_MO01)
C8210_SI01_MO01 | TA14 | Exturder Sifter 1-Motor | [5 empty] | 1 | [17 empty] | C8210_SCW06_MO01
C8210_SI02_MO01 | TA15 | Exturder Sifter 2-Motor | [5 empty] | 1 | [17 empty] | C8210_SCW06_MO01
C8210_SCW06_MO01 | T22 | Sifter Discharge Screw Extruder-Motor |  | 1 | [11 empty] | 1 | 1 | [11 empty] | Magnet Door Open
C8210_FA05_MO01 | VE29 | Loss-in-Weight Buffer Tank Fan-Motor
C8210_CN01_MO01 | T26 | Conveyor to LIW-Motor |  | 1 | [12 empty] | 1 | [11 empty] | LIW System Fault |  |  | V1.2 | Modified XINT1 Comment
C8210_FA06_MO01 | VE30 | Aspiration Fan LIW Conveyor-Motor
C8210_FA07_MO01 | VE31 | Aspiration Fan LIW Tank-Motor
C8210_LIW01_DO01 | TR07 | Loss-in-Weight System-Jesma Controller
C8210_LIW01_DO02 | TR07 | Loss-in-Weight System-Jesma Controller
C8210_SB01_MO01 | VF01 | LIW Tank Scarper Bottom-Motor
C8210_SCW07_MO01 | T27 | LIW Feed Screw-MOTOR | [5 empty] | 1 | 1 |  | 1 |  |  | 1 | [11 empty] | C8220_MX01_MO01 AND C8210_BV01_FB02 | [5 empty] | V1.2 | Added XPF
C8220_MX01_MO01 | COND01 | Pre-Conditioner 1-Motor |  |  | 1 |  |  | 1 |  | 1 |  | 1 | [13 empty] | C8220_MX02_MO01 | [5 empty] | V1.2 | Added XSS for Extruder Safety Circuits
C8220_MX02_MO01 | COND02 | Pre-Conditioner 2-Motor | [5 empty] | 1 |  |  | 1 | 1 | [13 empty] | C8220_EXT01_MO01 IF C8220_DV01_FB02 | [5 empty] | V1.2 | Added XSS for Extruder Safety Circuits
C8220_EXT01_MO01 | M04 | Extruder-Motor |  |  | 1 |  |  |  | 1 |  | 1 | 1 |  | 1 |  |  | 1 | 1 | 1 | [5 empty] | 2 Safety Systems |  | VSD Fault |  | Brush Fault | Motor Housing Open | Torque Limiter
C8220_FA01_MO01 | VE72 | Extruder Forced Ventilation-Motor | [6 empty] | 1 |  |  | 1 |  | 1 |  |  | 1 | [11 empty] | Pressure Switch |  |  | V1.2 | Added XSS for Extruder Safety Circuits
C8220_FA02_MO01 |  | Extruder Motor VSD Ventilation-Motor | [9 empty] | 1 |  | 1 | [17 empty] | V1.2 | Added XSS for Extruder Safety Circuits
C8220_HE01_DO01 | R02 | Extruder Heating-Elements
C8220_HY01_PU01_MO01 | M17 | Extruder Hydraulic Pump-Motor | [9 empty] | 1 |  | 1 | [17 empty] | V1.2 | Added XSS for Extruder Safety Circuits
C8220_PU01_MO01 | M02 | Extruder Lubrication Pump-Motor | [6 empty] | 1 |  |  | 1 |  | 1 |  |  | 1 | 1 | [6 empty] | 2 TTs |  |  |  | Pressure Switch | Oil Filter Fault |  | V1.2 | Added XSS for Extruder Safety Circuits
C8220_PU02_MO01 | M12 | Extruder Lubrication Pump Reduced-Motor | [9 empty] | 1 |  | 1 |  |  | 1 | [11 empty] | Pressure Switch |  |  | V1.2 | Added XSS for Extruder Safety Circuits
C8220_DZ01_MO01 | DEG | Degasser-Motor | [8 empty] | 1 | 1 | [14 empty] | VSD Fault |  |  |  |  | V1.2 | Added XSS for Extruder Safety Circuits
C8220_CU01_MO01 | GRA01 | Extruder Cutter-Motor | [7 empty] | 1 | 1 | 1 |  | 1 | [12 empty] | VSD Fault
C8224_FA01_MO01 | VE23 | Extruder Flash-Off Fan-Motor
C8224_RV01_MO01 | EC23 | Extruder Flash-Off Rotary Valve-Motor
C8226_CN01_MO01 | T51 | Extruder Conveyor-Motor | [5 empty] | 1 | [17 empty] | C8228_EV01_MO01
C8228_EV01_MO01 | E18 | Extruder Elevator-Motor | [5 empty] | 1 |  |  | 1 | [14 empty] | Dryer OK | Unipower Overload Protection Device |  |  |  |  | V1.2 | Moved from XRG to XPF (Overload Protection Device). Also added XDWN text
C8232_VB01_MO01 | AV01 | Vibro Conveyor after Dryer-Motor | [5 empty] | 1 | [5 empty] | 1 | [11 empty] | C8232_EV01_MO01
C8232_VB01_MO02 | AV01 | Vibro Conveyor after Dryer-Motor | [5 empty] | 1 | [5 empty] | 1 | [11 empty] | C8232_EV01_MO01 | [5 empty] | V1.2 | Moved from XRG to XPF (Overload Protection Device)
C8232_EV01_MO01 | E12 | Elevator after Dryer-Motor | [5 empty] | 1 |  |  | 1 |  |  | 1 | [12 empty] | Unipower Overload Protection Device
C8232_FA01_MO01 | VE32 | Elevator Aspiration Fan-Motor | [11 empty] | 1
C8234_SI01_MO01 | TA09 | Coater Sifter-Motor | [5 empty] | 1 | [5 empty] | 1 | [11 empty] | C8234_CN01_MO01
C8234_CN01_MO01 | T40 | Conveyor to Coater Pre-Bin-Motor |  |  | 1 | [8 empty] | 1 |  | 1
C8234_FA01_MO01 | VE70 | Vacuum Coater Aspiration Fan-Motor | [11 empty] | 1
C8234_SCW01_MO01 | T61 | Screw Conveyor to Waste-Motor | [5 empty] | 1 | [5 empty] | 1 | [11 empty] | C8270_DE01_MO01
C8235_PU01_MO01 | PO11 | Fish Oil Dosing Pump-Motor | [5 empty] | 1 |  |  | 1 |  |  | 1 | [11 empty] | C8235_BV01_FB02 | Tripped Breaker on VSD or VSD Fault |  |  |  |  | V1.2 | Modified PF Comments
C8235_PU02_MO01 | PO47 | Veg Oil Dosing Pump-Motor | [5 empty] | 1 |  |  | 1 |  |  | 1 | [11 empty] | C8235_BV02_FB02 | Tripped Breaker on VSD or VSD Fault |  |  |  |  | V1.2 | Modified PF Comments
C8235_PU03_MO01 | PO38 | Oil Trimmings Dosing Pump-Motor | [5 empty] | 1 |  |  | 1 |  |  | 1 | [11 empty] | C8235_BV03_FB02 | Tripped Breaker on VSD or VSD Fault |  |  |  |  | V1.2 | Modified PF Comments
C8236_PU01_MO01 | PO49 | Coater Fat Sealant Pump-Motor | [8 empty] | 1 | [15 empty] | VSD Fault
C8236_PU02_MO01 | PO39 | Coater Biol Pump-Motor | [5 empty] | 1 |  |  | 1 | [14 empty] | C8236_BV09_FB02 | Tripped Breaker on VSD or VSD Fault |  |  |  |  | V1.2 | Modified PF Comments
C8236_VC01_MX01_MO01 | M07 | Vacuum Coater Mixer-Motor | [8 empty] | 1 |  | 1 | 1 | [12 empty] | Tripped Breaker on VSD or VSD Fault |  |  |  |  | V1.2 | Modified PF Comments
C8236_VP01_MO01 | PO41 | Vacuum Pump 1-Motor | [10 empty] | 1 | 1
C8236_VP02_MO01 | PO42 | Vacuum Pump 2-Motor | [10 empty] | 1 | 1
C8238_VB01_MO01 | AV02 | Coater Discharge Vibro-Motor | [5 empty] | 1 |  |  | 1 |  |  | 1 | [11 empty] | C8238_EV01_MO01 | Tripped Breaker for common supply and thermal fault |  |  |  |  | V1.2 | Modified PF Comments
C8238_VB01_MO02 | AV02 | Coater Discharge Vibro-Motor | [5 empty] | 1 |  |  | 1 |  |  | 1 | [11 empty] | C8238_EV01_MO01 | Tripped Breaker for common supply and thermal fault |  |  |  |  | V1.2 | Modified PF Comments
C8238_EV01_MO01 | E17 | Elevator after Coater-Motor | [5 empty] | 1 |  |  | 1 |  |  | 1 | [11 empty] | Cooler Running | Unipower Overload Protection Device |  |  |  |  | V1.2 | Moved from XRG to XPF (Overload Protection Device). Also added XDWN text
C8243_VB01_MO01 | AV03 | Cooler Discharge Vibro-Motor | [5 empty] | 1 |  |  | 1 |  |  | 1 | [11 empty] | C8243_EV01_MO01 | Tripped Breaker for common supply and thermal fault |  |  |  |  | V1.2 | Modified PF Comments
C8243_VB01_MO02 | AV03 | Cooler Discharge Vibro-Motor | [5 empty] | 1 |  |  | 1 |  |  | 1 | [11 empty] | C8243_EV01_MO01 | Tripped Breaker for common supply and thermal fault |  |  |  |  | V1.2 | Modified PF Comments
C8243_EV01_MO01 | E21 | Elevator after Cooler-Motor | [5 empty] | 1 |  |  | 1 |  |  | 1 | [11 empty] | C8243_EV02_MO01 | Unipower Overload Protection Device |  |  |  |  | V1.2 | Moved from XRG to XPF (Overload Protection Device)
C8243_EV02_MO01 | E42 | Elevator to MVS-Motor | [5 empty] | 1 |  |  | 1 |  |  | 1 |  |  | 1 | [9 empty] | Unipower Overload Protection Device |  | Pressure Switch |  |  | V1.2 | Moved from XRG to XPF (Overload Protection Device)
C8250_DV01_LP01 | BD05 | Diverter After MVS-Lamp
C8250_DV01_LP02 | BD05 | Diverter After MVS-Lamp
C8250_VB01_MO01 | AV04 | Packing Vibro Feeder-Motor 1 | [5 empty] | 1 |  |  | 1 |  |  | 1 | [10 empty] | 2 PFs | C8250_SI01_MO01 AND C8250_VB01_MO02 | Tripped Breaker for common supply AND Power On Signal
C8250_VB01_MO02 | AV04 | Packing Vibro Feeder-Motor 2 | [5 empty] | 1 |  |  | 1 |  |  | 1 | [10 empty] | 2 PFs | C8250_SI01_MO01 AND C8250_VB01_MO02 | Tripped Breaker for common supply AND Power On Signal
C8250_SI01_MO01 | TA03 | Finished Product Sifter-Motor Left | [10 empty] | 1 | 1 |  |  | 1 | [9 empty] | Pressure Switch
C8250_SI01_MO02 | TA03 | Finished Product Sifter-Motor Right | [10 empty] | 1 | 1 |  |  | 1 | [9 empty] | Pressure Switch
C8251_EV01_MO01 | E08 | Elevator after MVS-Motor |  |  | 1 | [8 empty] | 1 | [17 empty] | V1.2 | Removed XOS
C8251_DB01_MO01 | DI07 | Semi-Finished Product Distributor-Start | [11 empty] | 1
C8252_CN01_MO01 | T20 | Conveyor to Packing Lines-Motor |  | 1
C8252_EV01_MO01 | E22 | Elevator from Packing Silos-Start |  |  | 1 |  |  |  |  | 1 |  |  |  | 1
C8259_MVS01_MO01 |  | MVS Sprayer-Motor |  |  | 1
C8259_MVS02_MO01 |  | MVS Spray Cylinder-Motor |  |  | 1
C8259_BL01_MO01 |  | MVS Blower-Motor | [11 empty] | 1
C8259_PU01_MO01 | 1DP1 | MVS Dosing Pump-Motor | [5 empty] | 1 | [7 empty] | 1 | [9 empty] | Valve Open (C8259_BV02 OR BV03. If BV03 then also BV04 OR BV05)
C8259_PU02_MO01 | 7VP1 | MVS Cold Oil Pump-Motor | [5 empty] | 1 | [17 empty] | C8259_BV07_FB02
C8259_PU03_MO01 | PO06 | MVS Oil Refill Pump-Motor | [5 empty] | 1 | [5 empty] | 1 | [11 empty] | C8259_BV09_FB02
C8259_PU04_MO01 | 15EPV5 | MVS Enzyme Dosing Pump-Motor | [13 empty] | 1
C8259_PU05_MO01 |  | MVS Enzyme Dosing Pump-Motor | [5 empty] | 1 | [17 empty] | C8259_BV10_FB02
C8259_CH01_DO01 |  | MVS Cooling System-Chillers
C8259_SCW01_MO01 |  | MVS Solid Feeder-Motor | [13 empty] | 1
C8260_CN01_MO01 | T28 | Conveyor to Big Bag Packing-Start |  | 1 | [8 empty] | 1 | 1
C8260_LF01_MO01 |  | Hoist for Big Bags-Start | [10 empty] | 1 | 1
C8260_FA01_MO01 | VE02 | Extract Fan - Big Bag-Start | [10 empty] | 1 | 1
C8260_BE01_MO01 | T29 | Conveyor after Big Bag Weighing-
C8270_DE01_MO01 | EX50 | Fines Recovery Disc Elevator-Motor |  |  | 1 | [11 empty] | 1 | [11 empty] | Chainguard
C8270_SCW01_MO01 | EX45 | Rework Dosing Screw-Motor | [14 empty] | 1 | [11 empty] | Scale Comms
C8822_CN01_MO01 | T19 | Conveyor to Crumbler-Start |  | 1 | [9 empty] | 1 |  | 1
C8822_SCW01_MO01 | CY03 | Feed Screw-Crumbler | [5 empty] | 1 | [5 empty] | 1 | [11 empty] | C8822_CM01_MO01
C8822_CM01_MO01 | CY03 | Pellet Crumbler-Crumbler | [5 empty] | 1 | [5 empty] | 1 | [11 empty] | C8828_SI01_MO01
C8822_CM01_MO02 | CY03 | Pellet Crumbler-Gap Adjustment Right | [11 empty] | 1
C8822_CM01_MO03 | CY03 | Pellet Crumbler-Gap Adjustment Left | [11 empty] | 1
C8828_SI01_MO01 | TA21 | Sifter After Crumbler- | [11 empty] | 1
C8828_DE01_MO01 | T76 | Disc Elevator Crumbling- | [11 empty] | 1
C8828_SCW01_MO01 | T77 | Screw Conveyor 1 Crumbling- | [5 empty] | 1 | [5 empty] | 1 | [11 empty] | C8828_SI02_MO01
C8828_SI02_MO01 | TA22 | Final Sifter- | [11 empty] | 1
C8828_FA01_MO01 | EC40 | Aspiration Fan- | [11 empty] | 1
C8828_FI01_MO01 | FI40 | Bagging Filter- | [14 empty] | 1 | [11 empty] | Blocked
C8833_RV01_MO01 | APIA | Rotary Valve-Motor | [11 empty] | 1
C8833_SCW01_MO01 | APIA | Transport Screw-Motor | [11 empty] | 1
C8835_TA01_MX01_MO01 | - | Liquid Tank Mixer-Crumbler | [11 empty] | 1
C8835_PU01_MO01 | - | Pump-Crumbler | [11 empty] | 1
C8836_MX01_MO01 | M06 | Micro Addition Mixer-Crumbler | [7 empty] | 1 |  | 1 |  | 1
C8838_VB01_MO01 | AV21 | Vibro Feeder to Bucket Packer-Motor | [5 empty] | 1 | [5 empty] | 1 | [11 empty] | C8838_EV01_MO01
C8838_EV01_MO01 | E74 | Elevator to Bucket Packer-Motor | [11 empty] | 1
C3301_PU01_MO01 | PO26 | Process Water Pump PreCon-Motor | [5 empty] | 1 |  |  | 1 | [14 empty] | C3301_BV01_FB02 | VSD Fault |  |  |  |  | V1.2 | Modified XDWN text
C3301_PU02_MO01 | PO13 | Process Water Pump Extruder-Motor | [8 empty] | 1
C3801_PU01_MO01 | PO01 | Oil Pump to Day Tank 3-Motor | [5 empty] | 1 | [17 empty] | C3801_BV01_FB02
C3801_PU02_MO01 | PO02 | Oil Pump to Day Tank 2-Motor | [5 empty] | 1 | [17 empty] | C3801_BV02_FB02
C3801_PU03_MO01 | PO03 | Oil Pump to Day Tank 1-Motor | [5 empty] | 1 | [17 empty] | C3801_BV03_FB02
C3802_TA01_MX01_MO01 | AG5.1 | Day Tank 1 Mixer-Motor | [11 empty] | 1
C3802_TA02_MX01_MO01 | AG02 | Day Tank 2 Mixer-Motor
C3802_TA03_MX01_MO01 | AG03 | Day Tank 3 Mixer-Motor
C3810_PU01_MO01 | PO13 | Oil Pump to Fat Sealant Buffer Tank-Motor | [8 empty] | 1 |  |  | 1 |  | 1 | [9 empty] | C3810_BV01_FB02 | VSD Fault
C3810_PU02_MO01 | PO46 | Fat Sealant Circulation Pump-Motor | [8 empty] | 1 | [15 empty] | VSD Fault
C3810_SO01_VB01 |  | Fat Sealant Flakes Silo-Vibro
C3810_EV01_MO01 |  | Fat Sealant Flakes Elevator-Motor
C3810_HE01_XX01 |  | Fat Sealant Heater-Stage 1
C3810_HE01_XX02 |  | Fat Sealant Heater-Stage 2
C3810_HE01_XX03 |  | Fat Sealant Heater-Stage 3
C3810_HE01_XX04 |  | Fat Sealant Heater-Stage 4
C3810_HE01_XX05 |  | Fat Sealant Heater-Stage 5
C3810_TA02_MX01_MO01 |  | Fat Sealant Tank Mixer-Motor | [8 empty] | 1 | [15 empty] | VSD Fault
C3810_TA02_HE01_XX01 |  | Fat Sealant Mixer Tank Heater-Stage 1
C3810_TA02_HE01_XX02 |  | Fat Sealant Mixer Tank Heater-Stage 2
C3820_PU01_MO01 | PO27 | Spare Oil Pump-Motor | [8 empty] | 1 | [15 empty] | VSD Fault
C3820_PU02_MO01 | PO48 | Oil Pump to Extruder-Motor
C3851_HE01_DO01 | L1.04 | Liquid Additive 1 Room Heater-Heating Controls
C3851_HE02_DO01 | L1.08 | Liquid Additive 1 Hose Heater-Heating Controls
C3851_HE03_DO01 | L1.13 | Liquid Additive 1 Pipe Heater-Heating Controls
C3851_PU01_MO01 | L1.02 | Liquid Additive 1 Pump-Motor | [5 empty] | 1 | [17 empty] | C3820_BV03_FB02
Note on AA17: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Telescopic pipe has its own Downstream, based on carousel position. Telescopic pipe is the only object looked at for XDWN
Note on AA41: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Tag doesn’t exist. Do you mean an extension of C8112_CN01_MO01?
Note on AA94: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Slidegate tags doesn’t exist
Note on AA159: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: IO?
Note on AA178: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: IO?
Note on AA186: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Should it be C8250_VB01_MO01 instead?
Note on A200: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Object missing in PLC
Note on A216: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Object missing in PLC
Note on A225: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Object missing in PLC

## Ignore Interlock in Manual
Tag | Old Tag | Description | XMG - Misalignment Guard | XOS - Overflow Switch | XRG - Rotation Guard | XFS - Flow Switch | XEX - Explosion Signal | XDWN - Downstream Signal | XTT - Temperature | XDS - Door Switch | XPF - Power Fault | XSS - Safety System | XIS - Isolator Fault | XMCB - Circuit Breaker Fault | XTH - Thermistor | XLS - Level Switch | XINT1 - Undefined | XINT2 - Undefined | XINT3 - Undefined | XINT4 - Undefined | XINT5 - Undefined | XINT6 - Undefined | XINT7 - Undefined | XINT8 - Undefined | External Block Comments | XDWN | PF Comments | MCB Comments | XINT1 Comment | XINT2 Comment | XINT3 Comment | Rev | Rev Comment
C8010_FA01_MO01 | VE13 | Bulk Intake Pit Extract Fan 1-Motor | [29 empty] | V1.2 | All shall be zero
C8010_FI01_DO01 | FI13 | Bulk Intake Pit Filter 1-Start Command | [29 empty] | V1.2 | All shall be zero
C8010_FA02_MO01 | VE14 | Bulk Intake Pit Extract Fan 2-Motor | [29 empty] | V1.2 | All shall be zero
C8010_FI02_DO01 | FI14 | Bulk Intake Pit Filter 2-Start Command | [29 empty] | V1.2 | All shall be zero
C8010_FA03_MO01 | VE15 | Bulk Intake Pit Extract Fan 3-Motor | [29 empty] | V1.2 | All shall be zero
C8010_FI03_DO01 | FI15 | Bulk Intake Pit Filter 3-Start Command | [29 empty] | V1.2 | All shall be zero
C8010_SCW01_MO01 | T01 | Bulk Intake Screw Conveyor 1-Motor | [29 empty] | V1.2 | All shall be zero
C8010_EV01_MO01 | E01 | Bulk Intake Elevator 1-Start | [29 empty] | V1.2 | All shall be zero
C8010_FA04_MO01 | VE18 | Bulk Intake Elevator 1 Fan-Motor | [29 empty] | V1.2 | All shall be zero
C8010_SCW02_MO01 | T02 | Bulk Intake Screw Conveyor 2-Motor | [29 empty] | V1.2 | All shall be zero
C8010_EV02_MO01 | E02 | Bulk Intake Elevator 2-Start | [29 empty] | V1.2 | All shall be zero
C8010_FA05_MO01 | VE19 | Bulk Intake Elevator 2 Fan-Motor | [29 empty] | V1.2 | All shall be zero
C8020_SCW01_MO01 | T03 | Silo Top Screw Conveyor 1-Motor | [29 empty] | V1.2 | All shall be zero
C8020_FA01_MO01 | VE20 | Silo Top Screw Conveyor 1 Fan-Motor | [29 empty] | V1.2 | All shall be zero
C8020_FI01_DO01 | FI20 | Silo Top Conveyor 1 Filter-Start Command | [29 empty] | V1.2 | All shall be zero
C8020_SCW02_MO01 | T04 | Silo Top Screw Conveyor 2-Motor | [29 empty] | V1.2 | All shall be zero
C8020_FA02_MO01 | VE21 | Silo Top Screw Conveyor 2 Fan-Motor | [29 empty] | V1.2 | All shall be zero
C8020_FI02_DO01 | FI21 | Silo Top Conveyor 2 Filter-Start Command | [29 empty] | V1.2 | All shall be zero
C8020_DB01_MO01 | RT04 | Silo Top Rotating Distributor-Motor | [29 empty] | V1.2 | All shall be zero
C8020_FI03_DO01 | FI33 | Bulk Silo 1 Filter-Start Command | [29 empty] | V1.2 | All shall be zero
C8020_FI04_DO01 | FI34 | Bulk Silo 4 Filter-Start Command | [29 empty] | V1.2 | All shall be zero
C8020_FA09_MO01 | VE31 | Bulk Silo 13 Fan-Motor | [29 empty] | V1.2 | All shall be zero
C8020_FI09_DO01 | FI31 | Bulk Silo 13 Filter-Start Command | [29 empty] | V1.2 | All shall be zero
C8020_FA07_MO01 | VE42 | Bulk Silo 15 Fan-Motor | [29 empty] | V1.2 | All shall be zero
C8020_FI07_DO01 | FI42 | Bulk Silo 15 Filter-Start Command | [29 empty] | V1.2 | All shall be zero
C8020_FA08_MO01 | VE41 | Bulk Silo 16 Fan-Motor | [29 empty] | V1.2 | All shall be zero
C8020_FI08_DO01 | FI41 | Bulk Silo 16 Filter-Start Command | [29 empty] | V1.2 | All shall be zero
C8020_FA10_MO01 | VE16 | Bulk Silo 23-25 Fan 1-Motor | [29 empty] | V1.2 | All shall be zero
C8020_FA11_MO01 | VE17 | Bulk Silo 23-25 Fan 2-Motor | [29 empty] | V1.2 | All shall be zero
C8020_CN01_MO01 | T65 | Silo Top Chain Conveyor 1-Motor | [29 empty] | V1.2 | All shall be zero
C8020_FI05_DO01 | FI35 | Bulk Silo 7 Filter-Start Command | [29 empty] | V1.2 | All shall be zero
C8020_FI06_DO01 | FI36 | Bulk Silo 8 Filter-Start Command | [29 empty] | V1.2 | All shall be zero
C8040_FA01_MO01 | VE20 | Micro Dosing Room Extract Fan-Motor | [29 empty] | V1.2 | All shall be zero
C8040_FI01_DO01 | FI20 | Micro Dosing Filter-Start Command | [29 empty] | V1.2 | All shall be zero
C8040_LF01_MO01 | HOIST | Hoist at Top of Micro Silos-Motor Up/Down | [29 empty] | V1.2 | All shall be zero
C8040_LF01_MO02 | HOIST | Hoist at Top of Micro Silos-Motor Left/Right | [29 empty] | V1.2 | All shall be zero
C8040_LF01_MO03 | HOIST | Hoist at Top of Micro Silos-Motor Forward/Back | [29 empty] | V1.2 | All shall be zero
C8040_LF01_PB01_DO01 | HOIST | Level 0 Hoist Command-Level 0 Lamp Indication | [29 empty] | V1.2 | All shall be zero
C8040_LF01_PB02_DO02 | HOIST | Level 2 Hoist Command-Level 2 Lamp Indication | [29 empty] | V1.2 | All shall be zero
C8110_SCW01_MO01 | EX1 | Dosing Screw Silo 1-Motor | [29 empty] | V1.2 | All shall be zero
C8110_SCW02_MO01 | EX2 | Dosing Screw Silo 2-Motor | [29 empty] | V1.2 | All shall be zero
C8110_SCW03_MO01 | EX3 | Dosing Screw Silo 3-Motor | [29 empty] | V1.2 | All shall be zero
C8110_SCW04_MO01 | EX4 | Dosing Screw Silo 4-Motor | [29 empty] | V1.2 | All shall be zero
C8110_SCW05_MO01 | EX5 | Dosing Screw Silo 5-Motor | [29 empty] | V1.2 | All shall be zero
C8110_SCW06_MO01 | EX6 | Dosing Screw Silo 6-Motor | [29 empty] | V1.2 | All shall be zero
C8110_SCW07_MO01 | EX7 | Dosing Screw Silo 7-Motor | [29 empty] | V1.2 | All shall be zero
C8110_SCW08_MO01 | EX8 | Dosing Screw Silo 8-Motor | [29 empty] | V1.2 | All shall be zero
C8110_SCW09_MO01 | EX9 | Dosing Screw Silo 9-Motor | [29 empty] | V1.2 | All shall be zero
C8110_VB09_MO01 | EX9 | Dosing Vibro Silo 9-Motor | [29 empty] | V1.2 | All shall be zero
C8110_VB09_MO02 | EX9 | Dosing Vibro Silo 9-Motor | [29 empty] | V1.2 | All shall be zero
C8110_SCW10_MO01 | EX10 | Dosing Screw Silo 10-Motor | [29 empty] | V1.2 | All shall be zero
C8110_VB10_MO01 | EX10 | Dosing Vibro Silo 10-Motor | [29 empty] | V1.2 | All shall be zero
C8110_VB10_MO02 | EX10 | Dosing Vibro Silo 10-Motor | [29 empty] | V1.2 | All shall be zero
C8110_SCW13_MO01 | EX13 | Dosing Screw Silo 13-Motor | [29 empty] | V1.2 | All shall be zero
C8110_SCW14_MO01 | EX14 | Dosing Screw Silo 14-Motor | [29 empty] | V1.2 | All shall be zero
C8110_SCW15_MO01 | EX15 | Dosing Screw Silo 15-Motor | [29 empty] | V1.2 | All shall be zero
C8110_SCW16_MO01 | EX16 | Dosing Screw Silo 16-Motor | [29 empty] | V1.2 | All shall be zero
C8110_VB16_MO01 | EX16 | Dosing Vibro Silo 16-Motor | [29 empty] | V1.2 | All shall be zero
C8110_VB16_MO02 | EX16 | Dosing Vibro Silo 16-Motor | [29 empty] | V1.2 | All shall be zero
C8110_SCW17_MO01 | EX17 | Dosing Screw Silo 17-Motor | [29 empty] | V1.2 | All shall be zero
C8110_SCW18_MO01 | EX18 | Dosing Screw Silo 18-Motor | [29 empty] | V1.2 | All shall be zero
C8110_SCW19_MO01 | EX19 | Dosing Screw Silo 19-Motor | [29 empty] | V1.2 | All shall be zero
C8110_VB19_MO01 | EX19 | Dosing Vibro Silo 19-Motor | [29 empty] | V1.2 | All shall be zero
C8110_VB19_MO02 | EX19 | Dosing Vibro Silo 19-Motor | [29 empty] | V1.2 | All shall be zero
C8110_SCW20_MO01 | EX20 | Dosing Screw Silo 20-Motor | [29 empty] | V1.2 | All shall be zero
C8110_SCW23_MO01 | EX23 | Dosing Screw Silo 23-Motor | [29 empty] | V1.2 | All shall be zero
C8110_SCW24_MO01 | EX24 | Dosing Screw Silo 24-Motor | [29 empty] | V1.2 | All shall be zero
C8110_SCW25_MO01 | EX25 | Dosing Screw Silo 25-Motor | [29 empty] | V1.2 | All shall be zero
C8112_CN01_MO01 | T09 | Primary Dosing Scale Discharge Conveyor-Motor | [29 empty] | V1.2 | All shall be zero
C8112_FA01_MO01 | FT09 | Scale Discharge Conveyor Aspiration Fan-Motor | [29 empty] | V1.2 | All shall be zero
C8114_CN01_MO01 | T10 | Batch Transport Conveyor 1-Motor | [29 empty] | V1.2 | All shall be zero
C8114_FA01_MO01 | FT10 | Batch Transport Conveyor Aspiration Fan-Motor | [29 empty] | V1.2 | All shall be zero
C8114_EV01_MO01 | E03 | Batch Transport Elevator 1-Start | [29 empty] | V1.2 | All shall be zero
C8114_FA02_MO01 | FE3 | Batch Transport Elevator Aspiration Fan-Motor | [29 empty] | V1.2 | All shall be zero
C8120_MX01_MO01 | M02 | Pre-Mixer-Motor | [29 empty] | V1.2 | All shall be zero
C8122_SCW01_MO01 | AL01 | Grinder 1 Feed Screw-Motor | [29 empty] | V1.2 | All shall be zero
C8122_SCW01_MO02 | AL01 | Grinder 1 Feed Screw-Forced Ventilation Motor | [29 empty] | V1.2 | All shall be zero
C8122_CR01_MO01 | PB01 | Grinder 1 Lump Crusher-Motor | [29 empty] | V1.2 | All shall be zero
C8122_ML01_MO01 | BR01 | Grinder 1-Motor | [29 empty] | V1.2 | All shall be zero
C8122_ML01_SS02_LP01 | KA180 | Grinder 1 Door Safety System-Indication Lamp | [29 empty] | V1.2 | All shall be zero
C8122_FA01_MO01 | VE03 | Grinder 1 Extract Fan-Motor | [29 empty] | V1.2 | All shall be zero
C8122_SCW02_MO01 | AL02 | Grinder 2 Feed Screw-Motor | [29 empty] | V1.2 | All shall be zero
C8122_SCW02_MO02 | AL02 | Grinder 1 Feed Screw-Forced Ventilation Motor | [29 empty] | V1.2 | All shall be zero
C8122_CR02_MO01 | PB02 | Grinder 2 Lump Crusher-Motor | [29 empty] | V1.2 | All shall be zero
C8122_ML02_MO01 | BR02 | Grinder 2-Motor | [29 empty] | V1.2 | All shall be zero
C8122_ML02_SS02_LP01 | KA180 | Grinder 2 Door Safety System-Indication Lamp | [29 empty] | V1.2 | All shall be zero
C8122_FA02_MO01 | VE04 | Grinder 2 Extract Fan-Motor | [29 empty] | V1.2 | All shall be zero
C8124_RV01_MO01 | EC02 | Grinder 1 Rotary Valve-Motor | [29 empty] | V1.2 | All shall be zero
C8124_SCW01_MO01 | T13 | Grinder 1 Discharge Screw-Motor | [29 empty] | V1.2 | All shall be zero
C8124_RV02_MO01 | EC03 | Grinder 2 Rotary Valve-Motor | [29 empty] | V1.2 | All shall be zero
C8124_SCW02_MO01 | T14 | Grinder 2 Discharge Screw-Motor | [29 empty] | V1.2 | All shall be zero
C8130_FA01_MO01 | VE07 | Weigh Bin Extract Fan-Motor | [29 empty] | V1.2 | All shall be zero
C8130_SCW31_MO01 | EX7 | Dosing Screw Silo 31-Motor | [29 empty] | V1.2 | All shall be zero
C8130_SCW32_MO01 | EX8 | Dosing Screw Silo 32-Motor | [29 empty] | V1.2 | All shall be zero
C8130_SCW33_MO01 | EX9 | Dosing Screw Silo 33-Motor | [29 empty] | V1.2 | All shall be zero
C8130_SCW34_MO01 | EX10 | Dosing Screw Silo 34-Motor | [29 empty] | V1.2 | All shall be zero
C8140_SB55_MO01 | DE55 | Scraper Bottom Silo 55-Motor | [29 empty] | V1.2 | All shall be zero
C8140_SCW55_MO01 | EX55 | Dosing Screw Silo 55-Motor | [29 empty] | V1.2 | All shall be zero
C8140_SB56_MO01 | DE56 | Scraper Bottom Silo 56-Motor | [29 empty] | V1.2 | All shall be zero
C8140_SCW56_MO01 | EX56 | Dosing Screw Silo 56-Motor | [29 empty] | V1.2 | All shall be zero
C8140_SB57_MO01 | DE57 | Scraper Bottom Silo 57-Motor | [29 empty] | V1.2 | All shall be zero
C8140_SCW57_MO01 | EX57 | Dosing Screw Silo 57-Motor | [29 empty] | V1.2 | All shall be zero
C8140_SB58_MO01 | DE58 | Scraper Bottom Silo 58-Motor | [29 empty] | V1.2 | All shall be zero
C8140_SCW58_MO01 | EX58 | Dosing Screw Silo 58-Motor | [29 empty] | V1.2 | All shall be zero
C8140_SB59_MO01 | DE59 | Scraper Bottom Silo 59-Motor | [29 empty] | V1.2 | All shall be zero
C8140_SCW59_MO01 | EX59 | Dosing Screw Silo 59-Motor | [29 empty] | V1.2 | All shall be zero
C8140_SB60_MO01 | DE60 | Scraper Bottom Silo 60-Motor | [29 empty] | V1.2 | All shall be zero
C8140_SCW60_MO01 | EX60 | Dosing Screw Silo 60-Motor | [29 empty] | V1.2 | All shall be zero
C8140_SCW61_MO01 | EX61 | Dosing Screw Silo 61-Motor | [29 empty] | V1.2 | All shall be zero
C8140_SCW62_MO01 | EX62 | Dosing Screw Silo 62-Motor | [29 empty] | V1.2 | All shall be zero
C8140_SCW63_MO01 | EX63 | Dosing Screw Silo 63-Motor | [29 empty] | V1.2 | All shall be zero
C8140_SCW64_MO01 | EX64 | Dosing Screw Silo 64-Motor | [29 empty] | V1.2 | All shall be zero
C8140_SCW65_MO01 | EX65 | Dosing Screw Silo 65-Motor | [29 empty] | V1.2 | All shall be zero
C8140_SCW66_MO01 | EX66 | Dosing Screw Silo 66-Motor | [29 empty] | V1.2 | All shall be zero
C8140_SCW67_MO01 | EX67 | Dosing Screw Silo 67-Motor | [29 empty] | V1.2 | All shall be zero
C8140_SCW68_MO01 | EX68 | Dosing Screw Silo 68-Motor | [29 empty] | V1.2 | All shall be zero
C8142_HM01_SV02 |  | Hammer on Micro Scale 1-Solenoid Valve | [29 empty] | V1.2 | All shall be zero
C8142_MX01_MO01 | M08 | Micro Mixer-Motor | [29 empty] | V1.2 | All shall be zero
C8150_FA01_MO01 | VS02 | Main Mixer Aspiration Fan-Motor | [29 empty] | V1.2 | All shall be zero
C8150_FI01_SV02 | FI25 | Main Mixer Filter-Solenoid Valve | [29 empty] | V1.2 | All shall be zero
C8150_MX01_MO01 | M03 | Main Mixer-Motor | [29 empty] | V1.2 | All shall be zero
C8150_CN01_MO01 | T15 | Main Mixer Conveyor-Motor | [29 empty] | V1.2 | All shall be zero
C8152_EV01_MO01 | E05 | Mixer Elevator-Start | [29 empty] | V1.2 | All shall be zero
C8152_FA01_MO01 | FE5 | Mixer Elevator Aspiration Fan-Motor | [29 empty] | V1.2 | All shall be zero
C8152_DB01_MO01 | DI04 | Distributor - Extruder Pre-Bins-Motor | [29 empty] | V1.2 | All shall be zero
C8210_FA01_MO01 | FI51 | Exturder Pre-Bin 1 Aspiration Fan-Motor | [29 empty] | V1.2 | All shall be zero
C8210_FI01_SV02 | FI51 | Exturder Pre-Bin 1 Filter-Solenoid Valve | [29 empty] | V1.2 | All shall be zero
C8210_FA02_MO01 | FI52 | Exturder Pre-Bin 2 Aspiration Fan-Motor | [29 empty] | V1.2 | All shall be zero
C8210_FI02_SV02 | FI52 | Exturder Pre-Bin 2 Filter-Solenoid Valve | [29 empty] | V1.2 | All shall be zero
C8210_SCW01_MO01 | EX41 | Discharge Screw Extruder Pre-Bin 1-Motor | [29 empty] | V1.2 | All shall be zero
C8210_SCW02_MO01 | EX42 | Discharge Screw Extruder Pre-Bin 2-Motor | [29 empty] | V1.2 | All shall be zero
C8210_SCW05_MO01 | T08 | Discharge Screw Extruder Pre-Bins-Motor | [29 empty] | V1.2 | All shall be zero
C8210_SI01_MO01 | TA14 | Exturder Sifter 1-Motor | [29 empty] | V1.2 | All shall be zero
C8210_SI02_MO01 | TA15 | Exturder Sifter 2-Motor | [29 empty] | V1.2 | All shall be zero
C8210_SCW06_MO01 | T22 | Sifter Discharge Screw Extruder-Motor | [29 empty] | V1.2 | All shall be zero
C8210_FA05_MO01 | VE29 | Loss-in-Weight Buffer Tank Fan-Motor | [29 empty] | V1.2 | All shall be zero
C8210_CN01_MO01 | T26 | Conveyor to LIW-Motor | [29 empty] | V1.2 | All shall be zero
C8210_FA06_MO01 | VE30 | Aspiration Fan LIW Conveyor-Motor | [29 empty] | V1.2 | All shall be zero
C8210_FA07_MO01 | VE31 | Aspiration Fan LIW Tank-Motor | [29 empty] | V1.2 | All shall be zero
C8210_LIW01_DO01 | TR07 | Loss-in-Weight System-Jesma Controller | [29 empty] | V1.2 | All shall be zero
C8210_LIW01_DO02 | TR07 | Loss-in-Weight System-Jesma Controller | [29 empty] | V1.2 | All shall be zero
C8210_SB01_MO01 | VF01 | LIW Tank Scarper Bottom-Motor | [29 empty] | V1.2 | All shall be zero
C8210_SCW07_MO01 | T27 | LIW Feed Screw-MOTOR | [29 empty] | V1.2 | All shall be zero
C8220_MX01_MO01 | COND01 | Pre-Conditioner 1-Motor | [29 empty] | V1.2 | All shall be zero
C8220_MX02_MO01 | COND02 | Pre-Conditioner 2-Motor | [29 empty] | V1.2 | All shall be zero
C8220_EXT01_MO01 | M04 | Extruder-Motor | [29 empty] | V1.2 | All shall be zero
C8220_FA01_MO01 | VE72 | Extruder Forced Ventilation-Motor | [29 empty] | V1.2 | All shall be zero
C8220_FA02_MO01 |  | Extruder Motor VSD Ventilation-Motor | [29 empty] | V1.2 | All shall be zero
C8220_HE01_DO01 | R02 | Extruder Heating-Elements | [29 empty] | V1.2 | All shall be zero
C8220_HY01_PU01_MO01 | M17 | Extruder Hydraulic Pump-Motor | [29 empty] | V1.2 | All shall be zero
C8220_PU01_MO01 | M02 | Extruder Lubrication Pump-Motor | [29 empty] | V1.2 | All shall be zero
C8220_PU02_MO01 | M12 | Extruder Lubrication Pump Reduced-Motor | [29 empty] | V1.2 | All shall be zero
C8220_DZ01_MO01 | DEG | Degasser-Motor | [29 empty] | V1.2 | All shall be zero
C8220_CU01_MO01 | GRA01 | Extruder Cutter-Motor | [29 empty] | V1.2 | All shall be zero
C8224_FA01_MO01 | VE23 | Extruder Flash-Off Fan-Motor | [29 empty] | V1.2 | All shall be zero
C8224_RV01_MO01 | EC23 | Extruder Flash-Off Rotary Valve-Motor | [29 empty] | V1.2 | All shall be zero
C8226_CN01_MO01 | T51 | Extruder Conveyor-Motor | [29 empty] | V1.2 | All shall be zero
C8228_EV01_MO01 | E18 | Extruder Elevator-Motor | [29 empty] | V1.2 | All shall be zero
C8232_VB01_MO01 | AV01 | Vibro Conveyor after Dryer-Motor | [29 empty] | V1.2 | All shall be zero
C8232_VB01_MO02 | AV01 | Vibro Conveyor after Dryer-Motor | [29 empty] | V1.2 | All shall be zero
C8232_EV01_MO01 | E12 | Elevator after Dryer-Motor | [29 empty] | V1.2 | All shall be zero
C8232_FA01_MO01 | VE32 | Elevator Aspiration Fan-Motor | [29 empty] | V1.2 | All shall be zero
C8234_SI01_MO01 | TA09 | Coater Sifter-Motor | [29 empty] | V1.2 | All shall be zero
C8234_CN01_MO01 | T40 | Conveyor to Coater Pre-Bin-Motor | [29 empty] | V1.2 | All shall be zero
C8234_FA01_MO01 | VE70 | Vacuum Coater Aspiration Fan-Motor | [29 empty] | V1.2 | All shall be zero
C8234_SCW01_MO01 | T61 | Screw Conveyor to Waste-Motor | [29 empty] | V1.2 | All shall be zero
C8235_PU01_MO01 | PO11 | Fish Oil Dosing Pump-Motor | [29 empty] | V1.2 | All shall be zero
C8235_PU02_MO01 | PO47 | Veg Oil Dosing Pump-Motor | [29 empty] | V1.2 | All shall be zero
C8235_PU03_MO01 | PO38 | Oil Trimmings Dosing Pump-Motor | [29 empty] | V1.2 | All shall be zero
C8236_PU01_MO01 | PO49 | Coater Fat Sealant Pump-Motor | [29 empty] | V1.2 | All shall be zero
C8236_PU02_MO01 | PO39 | Coater Biol Pump-Motor | [29 empty] | V1.2 | All shall be zero
C8236_VC01_MX01_MO01 | M07 | Vacuum Coater Mixer-Motor | [29 empty] | V1.2 | All shall be zero
C8236_VP01_MO01 | PO41 | Vacuum Pump 1-Motor | [29 empty] | V1.2 | All shall be zero
C8236_VP02_MO01 | PO42 | Vacuum Pump 2-Motor | [29 empty] | V1.2 | All shall be zero
C8238_VB01_MO01 | AV02 | Coater Discharge Vibro-Motor | [29 empty] | V1.2 | All shall be zero
C8238_VB01_MO02 | AV02 | Coater Discharge Vibro-Motor | [29 empty] | V1.2 | All shall be zero
C8238_EV01_MO01 | E17 | Elevator after Coater-Motor | [29 empty] | V1.2 | All shall be zero
C8243_VB01_MO01 | AV03 | Cooler Discharge Vibro-Motor | [29 empty] | V1.2 | All shall be zero
C8243_VB01_MO02 | AV03 | Cooler Discharge Vibro-Motor | [29 empty] | V1.2 | All shall be zero
C8243_EV01_MO01 | E21 | Elevator after Cooler-Motor | [29 empty] | V1.2 | All shall be zero
C8243_EV02_MO01 | E42 | Elevator to MVS-Motor | [29 empty] | V1.2 | All shall be zero
C8250_DV01_LP01 | BD05 | Diverter After MVS-Lamp | [29 empty] | V1.2 | All shall be zero
C8250_DV01_LP02 | BD05 | Diverter After MVS-Lamp | [29 empty] | V1.2 | All shall be zero
C8250_VB01_MO01 | AV04 | Packing Vibro Feeder-Motor 1 | [29 empty] | V1.2 | All shall be zero
C8250_VB01_MO02 | AV04 | Packing Vibro Feeder-Motor 2 | [29 empty] | V1.2 | All shall be zero
C8250_SI01_MO01 | TA03 | Finished Product Sifter-Motor Left | [29 empty] | V1.2 | All shall be zero
C8250_SI01_MO02 | TA03 | Finished Product Sifter-Motor Right | [29 empty] | V1.2 | All shall be zero
C8251_EV01_MO01 | E08 | Elevator after MVS-Motor | [29 empty] | V1.2 | All shall be zero
C8251_DB01_MO01 | DI07 | Semi-Finished Product Distributor-Start | [29 empty] | V1.2 | All shall be zero
C8252_CN01_MO01 | T20 | Conveyor to Packing Lines-Motor | [29 empty] | V1.2 | All shall be zero
C8252_EV01_MO01 | E22 | Elevator from Packing Silos-Start | [29 empty] | V1.2 | All shall be zero
C8259_MVS01_MO01 |  | MVS Sprayer-Motor | [29 empty] | V1.2 | All shall be zero
C8259_MVS02_MO01 |  | MVS Spray Cylinder-Motor | [29 empty] | V1.2 | All shall be zero
C8259_BL01_MO01 |  | MVS Blower-Motor | [29 empty] | V1.2 | All shall be zero
C8259_PU01_MO01 | 1DP1 | MVS Dosing Pump-Motor | [29 empty] | V1.2 | All shall be zero
C8259_PU02_MO01 | 7VP1 | MVS Cold Oil Pump-Motor | [29 empty] | V1.2 | All shall be zero
C8259_PU03_MO01 | PO06 | MVS Oil Refill Pump-Motor | [29 empty] | V1.2 | All shall be zero
C8259_PU04_MO01 | 15EPV5 | MVS Enzyme Dosing Pump-Motor | [29 empty] | V1.2 | All shall be zero
C8259_PU05_MO01 |  | MVS Enzyme Dosing Pump-Motor | [29 empty] | V1.2 | All shall be zero
C8259_CH01_DO01 |  | MVS Cooling System-Chillers | [29 empty] | V1.2 | All shall be zero
C8259_SCW01_MO01 |  | MVS Solid Feeder-Motor | [29 empty] | V1.2 | All shall be zero
C8260_CN01_MO01 | T28 | Conveyor to Big Bag Packing-Start | [29 empty] | V1.2 | All shall be zero
C8260_LF01_MO01 |  | Hoist for Big Bags-Start | [29 empty] | V1.2 | All shall be zero
C8260_FA01_MO01 | VE02 | Extract Fan - Big Bag-Start | [29 empty] | V1.2 | All shall be zero
C8260_BE01_MO01 | T29 | Conveyor after Big Bag Weighing- | [29 empty] | V1.2 | All shall be zero
C8270_DE01_MO01 | EX50 | Fines Recovery Disc Elevator-Motor | [29 empty] | V1.2 | All shall be zero
C8270_SCW01_MO01 | EX45 | Rework Dosing Screw-Motor | [29 empty] | V1.2 | All shall be zero
C8822_CN01_MO01 | T19 | Conveyor to Crumbler-Start | [29 empty] | V1.2 | All shall be zero
C8822_SCW01_MO01 | CY03 | Feed Screw-Crumbler | [29 empty] | V1.2 | All shall be zero
C8822_CM01_MO01 | CY03 | Pellet Crumbler-Crumbler | [29 empty] | V1.2 | All shall be zero
C8822_CM01_MO02 | CY03 | Pellet Crumbler-Gap Adjustment Right | [29 empty] | V1.2 | All shall be zero
C8822_CM01_MO03 | CY03 | Pellet Crumbler-Gap Adjustment Left | [29 empty] | V1.2 | All shall be zero
C8828_SI01_MO01 | TA21 | Sifter After Crumbler- | [29 empty] | V1.2 | All shall be zero
C8828_DE01_MO01 | T76 | Disc Elevator Crumbling- | [29 empty] | V1.2 | All shall be zero
C8828_SCW01_MO01 | T77 | Screw Conveyor 1 Crumbling- | [29 empty] | V1.2 | All shall be zero
C8828_SI02_MO01 | TA22 | Final Sifter- | [29 empty] | V1.2 | All shall be zero
C8828_FA01_MO01 | EC40 | Aspiration Fan- | [29 empty] | V1.2 | All shall be zero
C8828_FI01_MO01 | FI40 | Bagging Filter- | [29 empty] | V1.2 | All shall be zero
C8833_RV01_MO01 | APIA | Rotary Valve-Motor | [29 empty] | V1.2 | All shall be zero
C8833_SCW01_MO01 | APIA | Transport Screw-Motor | [29 empty] | V1.2 | All shall be zero
C8835_TA01_MX01_MO01 | - | Liquid Tank Mixer-Crumbler | [29 empty] | V1.2 | All shall be zero
C8835_PU01_MO01 | - | Pump-Crumbler | [29 empty] | V1.2 | All shall be zero
C8836_MX01_MO01 | M06 | Micro Addition Mixer-Crumbler | [29 empty] | V1.2 | All shall be zero
C8838_VB01_MO01 | AV21 | Vibro Feeder to Bucket Packer-Motor | [29 empty] | V1.2 | All shall be zero
C8838_EV01_MO01 | E74 | Elevator to Bucket Packer-Motor | [29 empty] | V1.2 | All shall be zero
C3301_PU01_MO01 | PO26 | Process Water Pump PreCon-Motor | [29 empty] | V1.2 | All shall be zero
C3301_PU02_MO01 | PO13 | Process Water Pump Extruder-Motor | [29 empty] | V1.2 | All shall be zero
C3801_PU01_MO01 | PO01 | Oil Pump to Day Tank 3-Motor | [29 empty] | V1.2 | All shall be zero
C3801_PU02_MO01 | PO02 | Oil Pump to Day Tank 2-Motor | [29 empty] | V1.2 | All shall be zero
C3801_PU03_MO01 | PO03 | Oil Pump to Day Tank 1-Motor | [29 empty] | V1.2 | All shall be zero
C3802_TA01_MX01_MO01 | AG5.1 | Day Tank 1 Mixer-Motor | [29 empty] | V1.2 | All shall be zero
C3802_TA02_MX01_MO01 | AG02 | Day Tank 2 Mixer-Motor | [29 empty] | V1.2 | All shall be zero
C3802_TA03_MX01_MO01 | AG03 | Day Tank 3 Mixer-Motor | [29 empty] | V1.2 | All shall be zero
C3810_PU01_MO01 | PO13 | Oil Pump to Fat Sealant Buffer Tank-Motor | [29 empty] | V1.2 | All shall be zero
C3810_PU02_MO01 | PO46 | Fat Sealant Circulation Pump-Motor | [29 empty] | V1.2 | All shall be zero
C3810_SO01_VB01 |  | Fat Sealant Flakes Silo-Vibro | [29 empty] | V1.2 | All shall be zero
C3810_EV01_MO01 |  | Fat Sealant Flakes Elevator-Motor | [29 empty] | V1.2 | All shall be zero
C3810_HE01_XX01 |  | Fat Sealant Heater-Stage 1 | [29 empty] | V1.2 | All shall be zero
C3810_HE01_XX02 |  | Fat Sealant Heater-Stage 2 | [29 empty] | V1.2 | All shall be zero
C3810_HE01_XX03 |  | Fat Sealant Heater-Stage 3 | [29 empty] | V1.2 | All shall be zero
C3810_HE01_XX04 |  | Fat Sealant Heater-Stage 4 | [29 empty] | V1.2 | All shall be zero
C3810_HE01_XX05 |  | Fat Sealant Heater-Stage 5 | [29 empty] | V1.2 | All shall be zero
C3810_TA02_MX01_MO01 |  | Fat Sealant Tank Mixer-Motor | [29 empty] | V1.2 | All shall be zero
C3810_TA02_HE01_XX01 |  | Fat Sealant Mixer Tank Heater-Stage 1 | [29 empty] | V1.2 | All shall be zero
C3810_TA02_HE01_XX02 |  | Fat Sealant Mixer Tank Heater-Stage 2 | [29 empty] | V1.2 | All shall be zero
C3820_PU01_MO01 | PO27 | Spare Oil Pump-Motor | [29 empty] | V1.2 | All shall be zero
C3820_PU02_MO01 | PO48 | Oil Pump to Extruder-Motor | [29 empty] | V1.2 | All shall be zero
C3851_HE01_DO01 | L1.04 | Liquid Additive 1 Room Heater-Heating Controls | [29 empty] | V1.2 | All shall be zero
C3851_HE02_DO01 | L1.08 | Liquid Additive 1 Hose Heater-Heating Controls | [29 empty] | V1.2 | All shall be zero
C3851_HE03_DO01 | L1.13 | Liquid Additive 1 Pipe Heater-Heating Controls | [29 empty] | V1.2 | All shall be zero
C3851_PU01_MO01 | L1.02 | Liquid Additive 1 Pump-Motor | [29 empty] | V1.2 | All shall be zero

## Can Be Disabled
Tag | Old Tag | Description | XMG - Misalignment Guard | XOS - Overflow Switch | XRG - Rotation Guard | XFS - Flow Switch | XEX - Explosion Signal | XDWN - Downstream Signal | XTT - Temperature | XDS - Door Switch | XPF - Power Fault | XSS - Safety System | XIS - Isolator Fault | XMCB - Circuit Breaker Fault | XTH - Thermistor | XLS - Level Switch | XINT1 - Undefined | XINT2 - Undefined | XINT3 - Undefined | XINT4 - Undefined | XINT5 - Undefined | XINT6 - Undefined | XINT7 - Undefined | XINT8 - Undefined | External Block Comments | XDWN | PF Comments | MCB Comments | XINT1 Comment | XINT2 Comment | XINT3 Comment
C8010_FA01_MO01 | VE13 | Bulk Intake Pit Extract Fan 1-Motor | [11 empty] | 1
C8010_FI01_DO01 | FI13 | Bulk Intake Pit Filter 1-Start Command
C8010_FA02_MO01 | VE14 | Bulk Intake Pit Extract Fan 2-Motor | [11 empty] | 1
C8010_FI02_DO01 | FI14 | Bulk Intake Pit Filter 2-Start Command
C8010_FA03_MO01 | VE15 | Bulk Intake Pit Extract Fan 3-Motor | [11 empty] | 1
C8010_FI03_DO01 | FI15 | Bulk Intake Pit Filter 3-Start Command
C8010_SCW01_MO01 | T01 | Bulk Intake Screw Conveyor 1-Motor |  | 1 |  |  |  | 1 | [5 empty] | 1 | [11 empty] | C8010_EV01_MO01
C8010_EV01_MO01 | E01 | Bulk Intake Elevator 1-Start | 1 |  | 1 |  |  | 1 | [5 empty] | 1 | [10 empty] | 4 MGs | C8010_SCW02_MO01
C8010_FA04_MO01 | VE18 | Bulk Intake Elevator 1 Fan-Motor | [11 empty] | 1
C8010_SCW02_MO01 | T02 | Bulk Intake Screw Conveyor 2-Motor |  | 1 |  |  |  | 1 | [5 empty] | 1 | [11 empty] | C8010_EV02_MO01
C8010_EV02_MO01 | E02 | Bulk Intake Elevator 2-Start | 1 |  | 1 |  |  | 1 | [5 empty] | 1 | [10 empty] | 4 MGs | C8020_SCW01_MO01 OR C8020_CN01_MO01 depending on position of C8020_DV01
C8010_FA05_MO01 | VE19 | Bulk Intake Elevator 2 Fan-Motor | [11 empty] | 1
C8020_SCW01_MO01 | T03 | Silo Top Screw Conveyor 1-Motor |  | 1 |  |  |  | 1 | [5 empty] | 1 | [11 empty] | C8020_SCW02_MO01
C8020_FA01_MO01 | VE20 | Silo Top Screw Conveyor 1 Fan-Motor | [11 empty] | 1
C8020_FI01_DO01 | FI20 | Silo Top Conveyor 1 Filter-Start Command
C8020_SCW02_MO01 | T04 | Silo Top Screw Conveyor 2-Motor |  | 1 |  |  |  | 1 | [5 empty] | 1 | [10 empty] | 2 Overflow Switches, one at each end | C8020_DP01_FB02 OR C8020_DP02_FB02 telescopic pipe extended AND C8020_SG0X_FB02 (X=Destination Silo)
C8020_FA02_MO01 | VE21 | Silo Top Screw Conveyor 2 Fan-Motor | [11 empty] | 1
C8020_FI02_DO01 | FI21 | Silo Top Conveyor 2 Filter-Start Command
C8020_DB01_MO01 | RT04 | Silo Top Rotating Distributor-Motor | [11 empty] | 1 |  |  | 1 | 1 | [10 empty] | Endstop Right | Endstop Left
C8020_FI03_DO01 | FI33 | Bulk Silo 1 Filter-Start Command
C8020_FI04_DO01 | FI34 | Bulk Silo 4 Filter-Start Command
C8020_FA09_MO01 | VE31 | Bulk Silo 13 Fan-Motor | [11 empty] | 1
C8020_FI09_DO01 | FI31 | Bulk Silo 13 Filter-Start Command
C8020_FA07_MO01 | VE42 | Bulk Silo 15 Fan-Motor | [11 empty] | 1
C8020_FI07_DO01 | FI42 | Bulk Silo 15 Filter-Start Command
C8020_FA08_MO01 | VE41 | Bulk Silo 16 Fan-Motor | [11 empty] | 1
C8020_FI08_DO01 | FI41 | Bulk Silo 16 Filter-Start Command
C8020_FA10_MO01 | VE16 | Bulk Silo 23-25 Fan 1-Motor | [11 empty] | 1
C8020_FA11_MO01 | VE17 | Bulk Silo 23-25 Fan 2-Motor | [11 empty] | 1
C8020_CN01_MO01 | T65 | Silo Top Chain Conveyor 1-Motor |  | 1 |  | 1 |  | 1 | [5 empty] | 1 | [11 empty] | C8020_BV07_FB02 OR C8020_BV08_FB02 depending on position of C8020_DV02
C8020_FI05_DO01 | FI35 | Bulk Silo 7 Filter-Start Command
C8020_FI06_DO01 | FI36 | Bulk Silo 8 Filter-Start Command
C8040_FA01_MO01 | VE20 | Micro Dosing Room Extract Fan-Motor | [11 empty] | 1
C8040_FI01_DO01 | FI20 | Micro Dosing Filter-Start Command
C8040_LF01_MO01 | HOIST | Hoist at Top of Micro Silos-Motor Up/Down | [10 empty] | 1 | 1
C8040_LF01_MO02 | HOIST | Hoist at Top of Micro Silos-Motor Left/Right | [10 empty] | 1 | 1
C8040_LF01_MO03 | HOIST | Hoist at Top of Micro Silos-Motor Forward/Back | [10 empty] | 1 | 1
C8040_LF01_PB01_DO01 | HOIST | Level 0 Hoist Command-Level 0 Lamp Indication
C8040_LF01_PB02_DO02 | HOIST | Level 2 Hoist Command-Level 2 Lamp Indication
C8110_SCW01_MO01 | EX1 | Dosing Screw Silo 1-Motor | [5 empty] | 1 |  |  | 1 | [5 empty] | 1 | [8 empty] | NOT C8112_CN01_XGH | Tripped Breaker on VSD |  | Scale Comms
C8110_SCW02_MO01 | EX2 | Dosing Screw Silo 2-Motor | [5 empty] | 1 |  |  | 1 | [5 empty] | 1 | [8 empty] | NOT C8112_CN01_XGH | Tripped Breaker on VSD |  | Scale Comms
C8110_SCW03_MO01 | EX3 | Dosing Screw Silo 3-Motor | [5 empty] | 1 |  |  | 1 | [5 empty] | 1 | [8 empty] | NOT C8112_CN01_XGH | Tripped Breaker on VSD |  | Scale Comms
C8110_SCW04_MO01 | EX4 | Dosing Screw Silo 4-Motor | [5 empty] | 1 |  |  | 1 | [5 empty] | 1 | [8 empty] | NOT C8112_CN01_XGH | Tripped Breaker on VSD |  | Scale Comms
C8110_SCW05_MO01 | EX5 | Dosing Screw Silo 5-Motor | [5 empty] | 1 |  |  | 1 | [5 empty] | 1 | [8 empty] | NOT C8112_CN01_XGH | Tripped Breaker on VSD |  | Scale Comms
C8110_SCW06_MO01 | EX6 | Dosing Screw Silo 6-Motor | [5 empty] | 1 |  |  | 1 | [5 empty] | 1 | [8 empty] | NOT C8112_CN01_XGH | Tripped Breaker on VSD |  | Scale Comms
C8110_SCW07_MO01 | EX7 | Dosing Screw Silo 7-Motor | [5 empty] | 1 |  |  | 1 | [5 empty] | 1 | [8 empty] | NOT C8112_CN01_XGH | Tripped Breaker on VSD |  | Scale Comms
C8110_SCW08_MO01 | EX8 | Dosing Screw Silo 8-Motor | [5 empty] | 1 |  |  | 1 | [5 empty] | 1 | [8 empty] | NOT C8112_CN01_XGH | Tripped Breaker on VSD |  | Scale Comms
C8110_SCW09_MO01 | EX9 | Dosing Screw Silo 9-Motor | [5 empty] | 1 |  |  | 1 | [5 empty] | 1 | [8 empty] | NOT C8112_CN01_XGH | Tripped Breaker on VSD |  | Scale Comms
C8110_VB09_MO01 | EX9 | Dosing Vibro Silo 9-Motor
C8110_VB09_MO02 | EX9 | Dosing Vibro Silo 9-Motor
C8110_SCW10_MO01 | EX10 | Dosing Screw Silo 10-Motor | [5 empty] | 1 |  |  | 1 | [5 empty] | 1 | [8 empty] | NOT C8112_CN01_XGH | Tripped Breaker on VSD |  | Scale Comms
C8110_VB10_MO01 | EX10 | Dosing Vibro Silo 10-Motor
C8110_VB10_MO02 | EX10 | Dosing Vibro Silo 10-Motor
C8110_SCW13_MO01 | EX13 | Dosing Screw Silo 13-Motor | [5 empty] | 1 |  |  | 1 | [5 empty] | 1 | [8 empty] | NOT C8112_CN01_XGH | Tripped Breaker on VSD |  | Scale Comms
C8110_SCW14_MO01 | EX14 | Dosing Screw Silo 14-Motor | [5 empty] | 1 |  |  | 1 | [5 empty] | 1 | [8 empty] | NOT C8112_CN01_XGH | Tripped Breaker on VSD |  | Scale Comms
C8110_SCW15_MO01 | EX15 | Dosing Screw Silo 15-Motor | [5 empty] | 1 |  |  | 1 | [5 empty] | 1 | [8 empty] | NOT C8112_CN01_XGH | Tripped Breaker on VSD |  | Scale Comms
C8110_SCW16_MO01 | EX16 | Dosing Screw Silo 16-Motor | [5 empty] | 1 |  |  | 1 | [5 empty] | 1 | [8 empty] | NOT C8112_CN01_XGH | Tripped Breaker on VSD |  | Scale Comms
C8110_VB16_MO01 | EX16 | Dosing Vibro Silo 16-Motor
C8110_VB16_MO02 | EX16 | Dosing Vibro Silo 16-Motor
C8110_SCW17_MO01 | EX17 | Dosing Screw Silo 17-Motor | [5 empty] | 1 |  |  | 1 | [5 empty] | 1 | [8 empty] | NOT C8112_CN01_XGH | Tripped Breaker on VSD |  | Scale Comms
C8110_SCW18_MO01 | EX18 | Dosing Screw Silo 18-Motor | [5 empty] | 1 |  |  | 1 | [5 empty] | 1 | [8 empty] | NOT C8112_CN01_XGH | Tripped Breaker on VSD |  | Scale Comms
C8110_SCW19_MO01 | EX19 | Dosing Screw Silo 19-Motor | [5 empty] | 1 |  |  | 1 | [5 empty] | 1 | [8 empty] | NOT C8112_CN01_XGH | Tripped Breaker on VSD |  | Scale Comms
C8110_VB19_MO01 | EX19 | Dosing Vibro Silo 19-Motor
C8110_VB19_MO02 | EX19 | Dosing Vibro Silo 19-Motor
C8110_SCW20_MO01 | EX20 | Dosing Screw Silo 20-Motor | [5 empty] | 1 |  |  | 1 | [5 empty] | 1 | [8 empty] | NOT C8112_CN01_XGH | Tripped Breaker on VSD |  | Scale Comms
C8110_SCW23_MO01 | EX23 | Dosing Screw Silo 23-Motor | [5 empty] | 1 |  |  | 1 | [5 empty] | 1 | [8 empty] | NOT C8112_CN01_XGH | Tripped Breaker on VSD |  | Scale Comms
C8110_SCW24_MO01 | EX24 | Dosing Screw Silo 24-Motor | [5 empty] | 1 |  |  | 1 | [5 empty] | 1 | [8 empty] | NOT C8112_CN01_XGH | Tripped Breaker on VSD |  | Scale Comms
C8110_SCW25_MO01 | EX25 | Dosing Screw Silo 25-Motor | [5 empty] | 1 |  |  | 1 | [5 empty] | 1 | [8 empty] | NOT C8112_CN01_XGH | Tripped Breaker on VSD |  | Scale Comms
C8112_CN01_MO01 | T09 | Primary Dosing Scale Discharge Conveyor-Motor |  | 1 |  |  |  | 1 | [17 empty] | C8114_CN01_MO01
C8112_FA01_MO01 | FT09 | Scale Discharge Conveyor Aspiration Fan-Motor
C8114_CN01_MO01 | T10 | Batch Transport Conveyor 1-Motor |  | 1 |  | 1 |  | 1 | [17 empty] | C8114_EV01_MO01
C8114_FA01_MO01 | FT10 | Batch Transport Conveyor Aspiration Fan-Motor
C8114_EV01_MO01 | E03 | Batch Transport Elevator 1-Start | 1 |  | 1 | [10 empty] | 1 | [8 empty] | 4 MGs
C8114_FA02_MO01 | FE3 | Batch Transport Elevator Aspiration Fan-Motor
C8120_MX01_MO01 | M02 | Pre-Mixer-Motor
C8122_SCW01_MO01 | AL01 | Grinder 1 Feed Screw-Motor |  | 1 |  |  |  | 1 | 1 |  |  |  |  | 1 | [11 empty] | C8122_CR01_MO01 |  | From VSD
C8122_SCW01_MO02 | AL01 | Grinder 1 Feed Screw-Forced Ventilation Motor | [11 empty] | 1
C8122_CR01_MO01 | PB01 | Grinder 1 Lump Crusher-Motor |  |  | 1 |  |  | 1 | 1 |  | 1 |  |  | 1 | [10 empty] | 2 TTs and 2 MCBs | C8122_ML01_MO01 | Soft Starter Fault
C8122_ML01_MO01 | BR01 | Grinder 1-Motor | [5 empty] | 1 | 1 | 1 | 1 | 1 |  | 1 | [10 empty] | 2 TTs and 2 MCBs | C8124_SCW01_MO01
C8122_ML01_SS02_LP01 | KA180 | Grinder 1 Door Safety System-Indication Lamp
C8122_FA01_MO01 | VE03 | Grinder 1 Extract Fan-Motor | [8 empty] | 1 |  |  | 1 | [12 empty] | VSD Fault
C8122_SCW02_MO01 | AL02 | Grinder 2 Feed Screw-Motor |  | 1 |  |  |  | 1 | 1 |  |  |  |  | 1 | [11 empty] | C8122_CR02_MO01 |  | From VSD
C8122_SCW02_MO02 | AL02 | Grinder 1 Feed Screw-Forced Ventilation Motor | [11 empty] | 1
C8122_CR02_MO01 | PB02 | Grinder 2 Lump Crusher-Motor |  |  | 1 |  |  | 1 | 1 |  | 1 |  |  | 1 | [10 empty] | 2 TTs and 2 MCBs | C8122_ML02_MO01 | Soft Starter Fault
C8122_ML02_MO01 | BR02 | Grinder 2-Motor | [5 empty] | 1 | 1 | 1 | 1 | 1 |  | 1 | [10 empty] | 2 TTs and 2 MCBs | C8124_SCW02_MO01
C8122_ML02_SS02_LP01 | KA180 | Grinder 2 Door Safety System-Indication Lamp
C8122_FA02_MO01 | VE04 | Grinder 2 Extract Fan-Motor | [8 empty] | 1 |  |  | 1 | [12 empty] | VSD Fault
C8124_RV01_MO01 | EC02 | Grinder 1 Rotary Valve-Motor
C8124_SCW01_MO01 | T13 | Grinder 1 Discharge Screw-Motor |  | 1 |  |  |  | 1 | [17 empty] | C8124_SCW01_MO01
C8124_RV02_MO01 | EC03 | Grinder 2 Rotary Valve-Motor
C8124_SCW02_MO01 | T14 | Grinder 2 Discharge Screw-Motor |  | 1 |  |  |  | 1 | [17 empty] | C8124_RV02_MO01
C8130_FA01_MO01 | VE07 | Weigh Bin Extract Fan-Motor
C8130_SCW31_MO01 | EX7 | Dosing Screw Silo 31-Motor | [5 empty] | 1 |  |  | 1 | [5 empty] | 1 | [8 empty] | NOT C8114_CN01_XGH | Tripped Breaker on VSD |  | Scale Comms
C8130_SCW32_MO01 | EX8 | Dosing Screw Silo 32-Motor | [5 empty] | 1 |  |  | 1 | [5 empty] | 1 | [8 empty] | NOT C8114_CN01_XGH | Tripped Breaker on VSD |  | Scale Comms
C8130_SCW33_MO01 | EX9 | Dosing Screw Silo 33-Motor | [5 empty] | 1 |  |  | 1 | [5 empty] | 1 | [8 empty] | NOT C8114_CN01_XGH | Tripped Breaker on VSD |  | Scale Comms
C8130_SCW34_MO01 | EX10 | Dosing Screw Silo 34-Motor | [5 empty] | 1 |  |  | 1 | [5 empty] | 1 | [8 empty] | NOT C8114_CN01_XGH | Tripped Breaker on VSD |  | Scale Comms
C8140_SB55_MO01 | DE55 | Scraper Bottom Silo 55-Motor | [10 empty] | 1 | 1
C8140_SCW55_MO01 | EX55 | Dosing Screw Silo 55-Motor | [5 empty] | 1 |  |  | 1 |  | 1 |  |  |  | 1 | [8 empty] | C8140_FV55_FB02 | Tripped Breaker on VSD |  | Scale Comms
C8140_SB56_MO01 | DE56 | Scraper Bottom Silo 56-Motor | [10 empty] | 1 | 1
C8140_SCW56_MO01 | EX56 | Dosing Screw Silo 56-Motor | [5 empty] | 1 |  |  | 1 |  | 1 |  |  |  | 1 | [8 empty] | C8140_FV56_FB02 | Tripped Breaker on VSD |  | Scale Comms
C8140_SB57_MO01 | DE57 | Scraper Bottom Silo 57-Motor | [10 empty] | 1 | 1
C8140_SCW57_MO01 | EX57 | Dosing Screw Silo 57-Motor | [5 empty] | 1 |  |  | 1 |  | 1 |  |  |  | 1 | [8 empty] | C8140_FV57_FB02 | Tripped Breaker on VSD |  | Scale Comms
C8140_SB58_MO01 | DE58 | Scraper Bottom Silo 58-Motor | [10 empty] | 1 | 1
C8140_SCW58_MO01 | EX58 | Dosing Screw Silo 58-Motor | [5 empty] | 1 |  |  | 1 |  | 1 |  |  |  | 1 | [8 empty] | C8140_FV58_FB02 | Tripped Breaker on VSD |  | Scale Comms
C8140_SB59_MO01 | DE59 | Scraper Bottom Silo 59-Motor | [10 empty] | 1 | 1
C8140_SCW59_MO01 | EX59 | Dosing Screw Silo 59-Motor | [5 empty] | 1 |  |  | 1 |  | 1 |  |  |  | 1 | [8 empty] | C8140_FV59_FB02 | Tripped Breaker on VSD |  | Scale Comms
C8140_SB60_MO01 | DE60 | Scraper Bottom Silo 60-Motor | [10 empty] | 1 | 1
C8140_SCW60_MO01 | EX60 | Dosing Screw Silo 60-Motor | [5 empty] | 1 |  |  | 1 |  | 1 |  |  |  | 1 | [8 empty] | C8140_FV60_FB02 | Tripped Breaker on VSD |  | Scale Comms
C8140_SCW61_MO01 | EX61 | Dosing Screw Silo 61-Motor | [5 empty] | 1 |  |  | 1 |  | 1 |  |  |  | 1 | [8 empty] | C8140_FV61_FB02 | Tripped Breaker on VSD |  | Scale Comms
C8140_SCW62_MO01 | EX62 | Dosing Screw Silo 62-Motor | [5 empty] | 1 |  |  | 1 |  | 1 |  |  |  | 1 | [8 empty] | C8140_FV62_FB02 | Tripped Breaker on VSD |  | Scale Comms
C8140_SCW63_MO01 | EX63 | Dosing Screw Silo 63-Motor | [5 empty] | 1 |  |  | 1 |  | 1 |  |  |  | 1 | [8 empty] | C8140_FV63_FB02 | Tripped Breaker on VSD |  | Scale Comms
C8140_SCW64_MO01 | EX64 | Dosing Screw Silo 64-Motor | [5 empty] | 1 |  |  | 1 |  | 1 |  |  |  | 1 | [8 empty] | C8140_FV64_FB02 | Tripped Breaker on VSD |  | Scale Comms
C8140_SCW65_MO01 | EX65 | Dosing Screw Silo 65-Motor | [5 empty] | 1 |  |  | 1 |  | 1 |  |  |  | 1 | [8 empty] | C8140_FV65_FB02 | Tripped Breaker on VSD |  | Scale Comms
C8140_SCW66_MO01 | EX66 | Dosing Screw Silo 66-Motor | [5 empty] | 1 |  |  | 1 |  | 1 |  |  |  | 1 | [8 empty] | C8140_FV66_FB02 | Tripped Breaker on VSD |  | Scale Comms
C8140_SCW67_MO01 | EX67 | Dosing Screw Silo 67-Motor | [5 empty] | 1 |  |  | 1 |  | 1 |  |  |  | 1 | [8 empty] | C8140_FV67_FB02 | Tripped Breaker on VSD |  | Scale Comms
C8140_SCW68_MO01 | EX68 | Dosing Screw Silo 68-Motor | [5 empty] | 1 |  |  | 1 |  | 1 |  |  |  | 1 | [8 empty] | C8140_FV68_FB02 | Tripped Breaker on VSD |  | Scale Comms
C8142_HM01_SV02 |  | Hammer on Micro Scale 1-Solenoid Valve
C8142_MX01_MO01 | M08 | Micro Mixer-Motor | [10 empty] | 1 | 1
C8150_FA01_MO01 | VS02 | Main Mixer Aspiration Fan-Motor
C8150_FI01_SV02 | FI25 | Main Mixer Filter-Solenoid Valve
C8150_MX01_MO01 | M03 | Main Mixer-Motor | [6 empty] | 1 | [5 empty] | 1
C8150_CN01_MO01 | T15 | Main Mixer Conveyor-Motor |  | 1 |  |  |  | 1 | [17 empty] | C8152_EV01_MO01
C8152_EV01_MO01 | E05 | Mixer Elevator-Start | 1 |  | 1 | [19 empty] | 4 MGs
C8152_FA01_MO01 | FE5 | Mixer Elevator Aspiration Fan-Motor
C8152_DB01_MO01 | DI04 | Distributor - Extruder Pre-Bins-Motor
C8210_FA01_MO01 | FI51 | Exturder Pre-Bin 1 Aspiration Fan-Motor
C8210_FI01_SV02 | FI51 | Exturder Pre-Bin 1 Filter-Solenoid Valve
C8210_FA02_MO01 | FI52 | Exturder Pre-Bin 2 Aspiration Fan-Motor
C8210_FI02_SV02 | FI52 | Exturder Pre-Bin 2 Filter-Solenoid Valve
C8210_SCW01_MO01 | EX41 | Discharge Screw Extruder Pre-Bin 1-Motor |  | 1 |  |  |  | 1 |  |  | 1 | [14 empty] | C8210_SCW05_MO01 | Tripped Breaker on VSD
C8210_SCW02_MO01 | EX42 | Discharge Screw Extruder Pre-Bin 2-Motor |  | 1 |  |  |  | 1 |  |  | 1 | [14 empty] | C8210_SCW05_MO01 | Tripped Breaker on VSD
C8210_SCW05_MO01 | T08 | Discharge Screw Extruder Pre-Bins-Motor |  | 1 |  |  |  | 1 | [17 empty] | C8210_SI01_MO01 OR C8210_SI02_MO01
C8210_SI01_MO01 | TA14 | Exturder Sifter 1-Motor | [5 empty] | 1 | [17 empty] | C8210_SCW06_MO01
C8210_SI02_MO01 | TA15 | Exturder Sifter 2-Motor | [5 empty] | 1 | [17 empty] | C8210_SCW06_MO01
C8210_SCW06_MO01 | T22 | Sifter Discharge Screw Extruder-Motor |  | 1 | [11 empty] | 1 | 1 | [11 empty] | Magnet Door Open
C8210_FA05_MO01 | VE29 | Loss-in-Weight Buffer Tank Fan-Motor
C8210_CN01_MO01 | T26 | Conveyor to LIW-Motor |  | 1 | [12 empty] | 1 | [11 empty] | Scale Comms
C8210_FA06_MO01 | VE30 | Aspiration Fan LIW Conveyor-Motor
C8210_FA07_MO01 | VE31 | Aspiration Fan LIW Tank-Motor
C8210_LIW01_DO01 | TR07 | Loss-in-Weight System-Jesma Controller
C8210_LIW01_DO02 | TR07 | Loss-in-Weight System-Jesma Controller
C8210_SB01_MO01 | VF01 | LIW Tank Scarper Bottom-Motor
C8210_SCW07_MO01 | T27 | LIW Feed Screw-MOTOR | [5 empty] | 1 | 1 |  |  |  |  | 1 | [11 empty] | C8220_MX01_MO01 AND C8210_BV01_FB02
C8220_MX01_MO01 | COND01 | Pre-Conditioner 1-Motor |  |  | 1 |  |  | 1 |  | 1 | [15 empty] | C8220_MX02_MO01
C8220_MX02_MO01 | COND02 | Pre-Conditioner 2-Motor | [5 empty] | 1 |  |  | 1
C8220_EXT01_MO01 | M04 | Extruder-Motor |  |  | 1 |  |  |  | 1 |  | 1 | 1 |  | 1 |  |  | 1 | 1 | 1 | [5 empty] | 2 Safety Systems | C8220_EXT01_MO01 IF C8220_DV01_FB02 | VSD Fault |  | Brush Fault | Motor Housing Open | Torque Limiter
C8220_FA01_MO01 | VE72 | Extruder Forced Ventilation-Motor | [6 empty] | 1 |  |  |  |  | 1 |  |  | 1 | [11 empty] | Pressure Switch
C8220_FA02_MO01 |  | Extruder Motor VSD Ventilation-Motor | [11 empty] | 1
C8220_HE01_DO01 | R02 | Extruder Heating-Elements
C8220_HY01_PU01_MO01 | M17 | Extruder Hydraulic Pump-Motor | [11 empty] | 1
C8220_PU01_MO01 | M02 | Extruder Lubrication Pump-Motor | [6 empty] | 1 |  |  |  |  | 1 |  |  | 1 | 1 | [6 empty] | 2 TTs |  |  |  | Pressure Switch | Oil Filter Fault
C8220_PU02_MO01 | M12 | Extruder Lubrication Pump Reduced-Motor | [11 empty] | 1 |  |  | 1 | [11 empty] | Pressure Switch
C8220_DZ01_MO01 | DEG | Degasser-Motor | [8 empty] | 1 | [15 empty] | VSD Fault
C8220_CU01_MO01 | GRA01 | Extruder Cutter-Motor | [7 empty] | 1 | 1 | 1 |  | 1 | [12 empty] | VSD Fault
C8224_FA01_MO01 | VE23 | Extruder Flash-Off Fan-Motor
C8224_RV01_MO01 | EC23 | Extruder Flash-Off Rotary Valve-Motor
C8226_CN01_MO01 | T51 | Extruder Conveyor-Motor | [5 empty] | 1 | [17 empty] | C8228_EV01_MO01
C8228_EV01_MO01 | E18 | Extruder Elevator-Motor | [5 empty] | 1 |  |  | 1 | [14 empty] | Dryer OK
C8232_VB01_MO01 | AV01 | Vibro Conveyor after Dryer-Motor | [5 empty] | 1 | [5 empty] | 1 | [11 empty] | C8232_EV01_MO01
C8232_VB01_MO02 | AV01 | Vibro Conveyor after Dryer-Motor | [5 empty] | 1 | [5 empty] | 1 | [11 empty] | C8232_EV01_MO01
C8232_EV01_MO01 | E12 | Elevator after Dryer-Motor |  |  | 1 |  |  | 1 | [5 empty] | 1
C8232_FA01_MO01 | VE32 | Elevator Aspiration Fan-Motor | [11 empty] | 1
C8234_SI01_MO01 | TA09 | Coater Sifter-Motor | [5 empty] | 1 | [5 empty] | 1 | [11 empty] | C8234_CN01_MO01
C8234_CN01_MO01 | T40 | Conveyor to Coater Pre-Bin-Motor |  |  | 1 | [8 empty] | 1 |  | 1
C8234_FA01_MO01 | VE70 | Vacuum Coater Aspiration Fan-Motor | [11 empty] | 1
C8234_SCW01_MO01 | T61 | Screw Conveyor to Waste-Motor | [5 empty] | 1 | [5 empty] | 1 | [11 empty] | C8270_DE01_MO01
C8235_PU01_MO01 | PO11 | Fish Oil Dosing Pump-Motor | [5 empty] | 1 |  |  | 1 |  |  | 1 | [11 empty] | C8235_BV01_FB02 | VSD Fault
C8235_PU02_MO01 | PO47 | Veg Oil Dosing Pump-Motor | [5 empty] | 1 |  |  | 1 |  |  | 1 | [11 empty] | C8235_BV02_FB02
C8235_PU03_MO01 | PO38 | Oil Trimmings Dosing Pump-Motor | [5 empty] | 1 |  |  | 1 |  |  | 1 | [11 empty] | C8235_BV03_FB02
C8236_PU01_MO01 | PO49 | Coater Fat Sealant Pump-Motor | [8 empty] | 1 | [15 empty] | VSD Fault
C8236_PU02_MO01 | PO39 | Coater Biol Pump-Motor | [5 empty] | 1 |  |  | 1 | [14 empty] | C8236_BV09_FB02 | VSD Fault
C8236_VC01_MX01_MO01 | M07 | Vacuum Coater Mixer-Motor | [8 empty] | 1 |  | 1 | 1 | [12 empty] | VSD Fault
C8236_VP01_MO01 | PO41 | Vacuum Pump 1-Motor | [10 empty] | 1 | 1
C8236_VP02_MO01 | PO42 | Vacuum Pump 2-Motor | [10 empty] | 1 | 1
C8238_VB01_MO01 | AV02 | Coater Discharge Vibro-Motor | [5 empty] | 1 |  |  | 1 |  |  | 1 | [11 empty] | C8238_EV01_MO01 | Tripped Breaker for common supply
C8238_VB01_MO02 | AV02 | Coater Discharge Vibro-Motor | [5 empty] | 1 |  |  | 1 |  |  | 1 | [11 empty] | C8238_EV01_MO01 | Tripped Breaker for common supply
C8238_EV01_MO01 | E17 | Elevator after Coater-Motor |  |  | 1 | [8 empty] | 1
C8243_VB01_MO01 | AV03 | Cooler Discharge Vibro-Motor | [5 empty] | 1 |  |  | 1 |  |  | 1 | [11 empty] | C8243_EV01_MO01 | Tripped Breaker for common supply
C8243_VB01_MO02 | AV03 | Cooler Discharge Vibro-Motor | [5 empty] | 1 |  |  | 1 |  |  | 1 | [11 empty] | C8243_EV01_MO01 | Tripped Breaker for common supply
C8243_EV01_MO01 | E21 | Elevator after Cooler-Motor |  |  | 1 |  |  | 1 | [5 empty] | 1 | [11 empty] | C8243_EV02_MO01
C8243_EV02_MO01 | E42 | Elevator to MVS-Motor |  |  | 1 | [8 empty] | 1 |  |  | 1 | [11 empty] | Pressure Switch
C8250_DV01_LP01 | BD05 | Diverter After MVS-Lamp
C8250_DV01_LP02 | BD05 | Diverter After MVS-Lamp
C8250_VB01_MO01 | AV04 | Packing Vibro Feeder-Motor 1 | [5 empty] | 1 |  |  | 1 |  |  | 1 | [10 empty] | 2 PFs | C8250_SI01_MO01 AND C8250_VB01_MO02 | Tripped Breaker for common supply AND Power On Signal
C8250_VB01_MO02 | AV04 | Packing Vibro Feeder-Motor 2 | [5 empty] | 1 |  |  | 1 |  |  | 1 | [10 empty] | 2 PFs | C8250_SI01_MO01 AND C8250_VB01_MO02 | Tripped Breaker for common supply AND Power On Signal
C8250_SI01_MO01 | TA03 | Finished Product Sifter-Motor Left | [10 empty] | 1 | 1 |  |  | 1 | [9 empty] | Pressure Switch
C8250_SI01_MO02 | TA03 | Finished Product Sifter-Motor Right | [10 empty] | 1 | 1 |  |  | 1 | [9 empty] | Pressure Switch
C8251_EV01_MO01 | E08 | Elevator after MVS-Motor |  | 1 | 1 | [8 empty] | 1
C8251_DB01_MO01 | DI07 | Semi-Finished Product Distributor-Start | [11 empty] | 1
C8252_CN01_MO01 | T20 | Conveyor to Packing Lines-Motor |  | 1
C8252_EV01_MO01 | E22 | Elevator from Packing Silos-Start |  |  | 1 |  |  |  |  | 1 |  |  |  | 1
C8259_MVS01_MO01 |  | MVS Sprayer-Motor |  |  | 1
C8259_MVS02_MO01 |  | MVS Spray Cylinder-Motor |  |  | 1
C8259_BL01_MO01 |  | MVS Blower-Motor | [11 empty] | 1
C8259_PU01_MO01 | 1DP1 | MVS Dosing Pump-Motor | [5 empty] | 1 | [7 empty] | 1 | [9 empty] | Valve Open (C8259_BV02 OR BV03. If BV03 then also BV04 OR BV05)
C8259_PU02_MO01 | 7VP1 | MVS Cold Oil Pump-Motor | [5 empty] | 1 | [17 empty] | C8259_BV07_FB02
C8259_PU03_MO01 | PO06 | MVS Oil Refill Pump-Motor | [5 empty] | 1 | [5 empty] | 1 | [11 empty] | C8259_BV09_FB02
C8259_PU04_MO01 | 15EPV5 | MVS Enzyme Dosing Pump-Motor | [13 empty] | 1
C8259_PU05_MO01 |  | MVS Enzyme Dosing Pump-Motor | [5 empty] | 1 | [17 empty] | C8259_BV10_FB02
C8259_CH01_DO01 |  | MVS Cooling System-Chillers
C8259_SCW01_MO01 |  | MVS Solid Feeder-Motor | [13 empty] | 1
C8260_CN01_MO01 | T28 | Conveyor to Big Bag Packing-Start |  | 1 | [8 empty] | 1 | 1
C8260_LF01_MO01 |  | Hoist for Big Bags-Start | [10 empty] | 1 | 1
C8260_FA01_MO01 | VE02 | Extract Fan - Big Bag-Start | [10 empty] | 1 | 1
C8260_BE01_MO01 | T29 | Conveyor after Big Bag Weighing-
C8270_DE01_MO01 | EX50 | Fines Recovery Disc Elevator-Motor |  |  | 1 | [11 empty] | 1 | [11 empty] | Chainguard
C8270_SCW01_MO01 | EX45 | Rework Dosing Screw-Motor | [14 empty] | 1 | [11 empty] | Scale Comms
C8822_CN01_MO01 | T19 | Conveyor to Crumbler-Start |  | 1 | [9 empty] | 1 |  | 1
C8822_SCW01_MO01 | CY03 | Feed Screw-Crumbler | [5 empty] | 1 | [5 empty] | 1 | [11 empty] | C8822_CM01_MO01
C8822_CM01_MO01 | CY03 | Pellet Crumbler-Crumbler | [5 empty] | 1 | [5 empty] | 1 | [11 empty] | C8828_SI01_MO01
C8822_CM01_MO02 | CY03 | Pellet Crumbler-Gap Adjustment Right | [11 empty] | 1
C8822_CM01_MO03 | CY03 | Pellet Crumbler-Gap Adjustment Left | [11 empty] | 1
C8828_SI01_MO01 | TA21 | Sifter After Crumbler- | [11 empty] | 1
C8828_DE01_MO01 | T76 | Disc Elevator Crumbling- | [11 empty] | 1
C8828_SCW01_MO01 | T77 | Screw Conveyor 1 Crumbling- | [5 empty] | 1 | [5 empty] | 1 | [11 empty] | C8828_SI02_MO01
C8828_SI02_MO01 | TA22 | Final Sifter- | [11 empty] | 1
C8828_FA01_MO01 | EC40 | Aspiration Fan- | [11 empty] | 1
C8828_FI01_MO01 | FI40 | Bagging Filter- | [14 empty] | 1 | [11 empty] | Blocked
C8833_RV01_MO01 | APIA | Rotary Valve-Motor | [11 empty] | 1
C8833_SCW01_MO01 | APIA | Transport Screw-Motor | [11 empty] | 1
C8835_TA01_MX01_MO01 | - | Liquid Tank Mixer-Crumbler | [11 empty] | 1
C8835_PU01_MO01 | - | Pump-Crumbler | [11 empty] | 1
C8836_MX01_MO01 | M06 | Micro Addition Mixer-Crumbler | [7 empty] | 1 |  | 1 |  | 1
C8838_VB01_MO01 | AV21 | Vibro Feeder to Bucket Packer-Motor | [5 empty] | 1 | [5 empty] | 1 | [11 empty] | C8838_EV01_MO01
C8838_EV01_MO01 | E74 | Elevator to Bucket Packer-Motor | [11 empty] | 1
C3301_PU01_MO01 | PO26 | Process Water Pump PreCon-Motor | [5 empty] | 1 |  |  | 1 | [14 empty] | C3601_BV01_FB02 | VSD Fault
C3301_PU02_MO01 | PO13 | Process Water Pump Extruder-Motor | [8 empty] | 1
C3801_PU01_MO01 | PO01 | Oil Pump to Day Tank 3-Motor | [5 empty] | 1 | [17 empty] | C3801_BV01_FB02
C3801_PU02_MO01 | PO02 | Oil Pump to Day Tank 2-Motor | [5 empty] | 1 | [17 empty] | C3801_BV02_FB02
C3801_PU03_MO01 | PO03 | Oil Pump to Day Tank 1-Motor | [5 empty] | 1 | [17 empty] | C3801_BV03_FB02
C3802_TA01_MX01_MO01 | AG5.1 | Day Tank 1 Mixer-Motor | [11 empty] | 1
C3802_TA02_MX01_MO01 | AG02 | Day Tank 2 Mixer-Motor
C3802_TA03_MX01_MO01 | AG03 | Day Tank 3 Mixer-Motor
C3810_PU01_MO01 | PO13 | Oil Pump to Fat Sealant Buffer Tank-Motor | [8 empty] | 1 |  |  | 1 |  | 1 | [9 empty] | C3810_BV01_FB02 | VSD Fault
C3810_PU02_MO01 | PO46 | Fat Sealant Circulation Pump-Motor | [8 empty] | 1 | [15 empty] | VSD Fault
C3810_SO01_VB01 |  | Fat Sealant Flakes Silo-Vibro
C3810_EV01_MO01 |  | Fat Sealant Flakes Elevator-Motor
C3810_HE01_XX01 |  | Fat Sealant Heater-Stage 1
C3810_HE01_XX02 |  | Fat Sealant Heater-Stage 2
C3810_HE01_XX03 |  | Fat Sealant Heater-Stage 3
C3810_HE01_XX04 |  | Fat Sealant Heater-Stage 4
C3810_HE01_XX05 |  | Fat Sealant Heater-Stage 5
C3810_TA02_MX01_MO01 |  | Fat Sealant Tank Mixer-Motor | [8 empty] | 1 | [15 empty] | VSD Fault
C3810_TA02_HE01_XX01 |  | Fat Sealant Mixer Tank Heater-Stage 1
C3810_TA02_HE01_XX02 |  | Fat Sealant Mixer Tank Heater-Stage 2
C3820_PU01_MO01 | PO27 | Spare Oil Pump-Motor | [8 empty] | 1 | [15 empty] | VSD Fault
C3820_PU02_MO01 | PO48 | Oil Pump to Extruder-Motor
C3851_HE01_DO01 | L1.04 | Liquid Additive 1 Room Heater-Heating Controls
C3851_HE02_DO01 | L1.08 | Liquid Additive 1 Hose Heater-Heating Controls
C3851_HE03_DO01 | L1.13 | Liquid Additive 1 Pipe Heater-Heating Controls
C3851_PU01_MO01 | L1.02 | Liquid Additive 1 Pump-Motor | [5 empty] | 1 | [17 empty] | C3820_BV03_FB02

## External Block Exists
Tag | Old Tag | Description | XMG - Misalignment Guard | XOS - Overflow Switch | XRG - Rotation Guard | XFS - Flow Switch | XEX - Explosion Signal | XDWN - Downstream Signal | XTT - Temperature | XDS - Door Switch | XPF - Power Fault | XSS - Safety System | XIS - Isolator Fault | XMCB - Circuit Breaker Fault | XTH - Thermistor | XLS - Level Switch | XINT1 - Undefined | XINT2 - Undefined | XINT3 - Undefined | XINT4 - Undefined | XINT5 - Undefined | XINT6 - Undefined | XINT7 - Undefined | XINT8 - Undefined | External Block Comments
C8010_FA01_MO01 | VE13 | Bulk Intake Pit Extract Fan 1-Motor
C8010_FI01_DO01 | FI13 | Bulk Intake Pit Filter 1-Start Command
C8010_FA02_MO01 | VE14 | Bulk Intake Pit Extract Fan 2-Motor
C8010_FI02_DO01 | FI14 | Bulk Intake Pit Filter 2-Start Command
C8010_FA03_MO01 | VE15 | Bulk Intake Pit Extract Fan 3-Motor
C8010_FI03_DO01 | FI15 | Bulk Intake Pit Filter 3-Start Command
C8010_SCW01_MO01 | T01 | Bulk Intake Screw Conveyor 1-Motor
C8010_EV01_MO01 | E01 | Bulk Intake Elevator 1-Start | 1 | [21 empty] | 4 MGs
C8010_FA04_MO01 | VE18 | Bulk Intake Elevator 1 Fan-Motor
C8010_SCW02_MO01 | T02 | Bulk Intake Screw Conveyor 2-Motor
C8010_EV02_MO01 | E02 | Bulk Intake Elevator 2-Start | 1 | [21 empty] | 4 MGs
C8010_FA05_MO01 | VE19 | Bulk Intake Elevator 2 Fan-Motor
C8020_SCW01_MO01 | T03 | Silo Top Screw Conveyor 1-Motor
C8020_FA01_MO01 | VE20 | Silo Top Screw Conveyor 1 Fan-Motor
C8020_FI01_DO01 | FI20 | Silo Top Conveyor 1 Filter-Start Command
C8020_SCW02_MO01 | T04 | Silo Top Screw Conveyor 2-Motor |  | 1 | [20 empty] | 2 Overflow Switches, one at each end
C8020_FA02_MO01 | VE21 | Silo Top Screw Conveyor 2 Fan-Motor
C8020_FI02_DO01 | FI21 | Silo Top Conveyor 2 Filter-Start Command
C8020_DB01_MO01 | RT04 | Silo Top Rotating Distributor-Motor
C8020_FI03_DO01 | FI33 | Bulk Silo 1 Filter-Start Command
C8020_FI04_DO01 | FI34 | Bulk Silo 4 Filter-Start Command
C8020_FA09_MO01 | VE31 | Bulk Silo 13 Fan-Motor
C8020_FI09_DO01 | FI31 | Bulk Silo 13 Filter-Start Command
C8020_FA07_MO01 | VE42 | Bulk Silo 15 Fan-Motor
C8020_FI07_DO01 | FI42 | Bulk Silo 15 Filter-Start Command
C8020_FA08_MO01 | VE41 | Bulk Silo 16 Fan-Motor
C8020_FI08_DO01 | FI41 | Bulk Silo 16 Filter-Start Command
C8020_FA10_MO01 | VE16 | Bulk Silo 23-25 Fan 1-Motor
C8020_FA11_MO01 | VE17 | Bulk Silo 23-25 Fan 2-Motor
C8020_CN01_MO01 | T65 | Silo Top Chain Conveyor 1-Motor
C8020_FI05_DO01 | FI35 | Bulk Silo 7 Filter-Start Command
C8020_FI06_DO01 | FI36 | Bulk Silo 8 Filter-Start Command
C8040_FA01_MO01 | VE20 | Micro Dosing Room Extract Fan-Motor
C8040_FI01_DO01 | FI20 | Micro Dosing Filter-Start Command
C8040_LF01_MO01 | HOIST | Hoist at Top of Micro Silos-Motor Up/Down | [22 empty] | 3 XSS
C8040_LF01_MO02 | HOIST | Hoist at Top of Micro Silos-Motor Left/Right | [22 empty] | 3 XSS
C8040_LF01_MO03 | HOIST | Hoist at Top of Micro Silos-Motor Forward/Back | [22 empty] | 3 XSS
C8040_LF01_PB01_DO01 | HOIST | Level 0 Hoist Command-Level 0 Lamp Indication
C8040_LF01_PB02_DO02 | HOIST | Level 2 Hoist Command-Level 2 Lamp Indication
C8110_SCW01_MO01 | EX1 | Dosing Screw Silo 1-Motor
C8110_SCW02_MO01 | EX2 | Dosing Screw Silo 2-Motor
C8110_SCW03_MO01 | EX3 | Dosing Screw Silo 3-Motor
C8110_SCW04_MO01 | EX4 | Dosing Screw Silo 4-Motor
C8110_SCW05_MO01 | EX5 | Dosing Screw Silo 5-Motor
C8110_SCW06_MO01 | EX6 | Dosing Screw Silo 6-Motor
C8110_SCW07_MO01 | EX7 | Dosing Screw Silo 7-Motor
C8110_SCW08_MO01 | EX8 | Dosing Screw Silo 8-Motor
C8110_SCW09_MO01 | EX9 | Dosing Screw Silo 9-Motor
C8110_VB09_MO01 | EX9 | Dosing Vibro Silo 9-Motor
C8110_VB09_MO02 | EX9 | Dosing Vibro Silo 9-Motor
C8110_SCW10_MO01 | EX10 | Dosing Screw Silo 10-Motor
C8110_VB10_MO01 | EX10 | Dosing Vibro Silo 10-Motor
C8110_VB10_MO02 | EX10 | Dosing Vibro Silo 10-Motor
C8110_SCW13_MO01 | EX13 | Dosing Screw Silo 13-Motor
C8110_SCW14_MO01 | EX14 | Dosing Screw Silo 14-Motor
C8110_SCW15_MO01 | EX15 | Dosing Screw Silo 15-Motor
C8110_SCW16_MO01 | EX16 | Dosing Screw Silo 16-Motor
C8110_VB16_MO01 | EX16 | Dosing Vibro Silo 16-Motor
C8110_VB16_MO02 | EX16 | Dosing Vibro Silo 16-Motor
C8110_SCW17_MO01 | EX17 | Dosing Screw Silo 17-Motor
C8110_SCW18_MO01 | EX18 | Dosing Screw Silo 18-Motor
C8110_SCW19_MO01 | EX19 | Dosing Screw Silo 19-Motor
C8110_VB19_MO01 | EX19 | Dosing Vibro Silo 19-Motor
C8110_VB19_MO02 | EX19 | Dosing Vibro Silo 19-Motor
C8110_SCW20_MO01 | EX20 | Dosing Screw Silo 20-Motor
C8110_SCW23_MO01 | EX23 | Dosing Screw Silo 23-Motor
C8110_SCW24_MO01 | EX24 | Dosing Screw Silo 24-Motor
C8110_SCW25_MO01 | EX25 | Dosing Screw Silo 25-Motor
C8112_CN01_MO01 | T09 | Primary Dosing Scale Discharge Conveyor-Motor
C8112_FA01_MO01 | FT09 | Scale Discharge Conveyor Aspiration Fan-Motor
C8114_CN01_MO01 | T10 | Batch Transport Conveyor 1-Motor
C8114_FA01_MO01 | FT10 | Batch Transport Conveyor Aspiration Fan-Motor
C8114_EV01_MO01 | E03 | Batch Transport Elevator 1-Start | 1 | [21 empty] | 4 MGs
C8114_FA02_MO01 | FE3 | Batch Transport Elevator Aspiration Fan-Motor
C8120_MX01_MO01 | M02 | Pre-Mixer-Motor
C8122_SCW01_MO01 | AL01 | Grinder 1 Feed Screw-Motor
C8122_SCW01_MO02 | AL01 | Grinder 1 Feed Screw-Forced Ventilation Motor
C8122_CR01_MO01 | PB01 | Grinder 1 Lump Crusher-Motor | [6 empty] | 1 |  |  |  |  | 1 | [10 empty] | 2 TTs and 2 MCBs
C8122_ML01_MO01 | BR01 | Grinder 1-Motor | [6 empty] | 1 |  |  |  |  | 1 | [10 empty] | 2 TTs and 2 MCBs
C8122_ML01_SS02_LP01 | KA180 | Grinder 1 Door Safety System-Indication Lamp
C8122_FA01_MO01 | VE03 | Grinder 1 Extract Fan-Motor
C8122_SCW02_MO01 | AL02 | Grinder 2 Feed Screw-Motor
C8122_SCW02_MO02 | AL02 | Grinder 1 Feed Screw-Forced Ventilation Motor
C8122_CR02_MO01 | PB02 | Grinder 2 Lump Crusher-Motor | [6 empty] | 1 |  |  |  |  | 1 | [10 empty] | 2 TTs and 2 MCBs
C8122_ML02_MO01 | BR02 | Grinder 2-Motor | [6 empty] | 1 |  |  |  |  | 1 | [10 empty] | 2 TTs and 2 MCBs
C8122_ML02_SS02_LP01 | KA180 | Grinder 2 Door Safety System-Indication Lamp
C8122_FA02_MO01 | VE04 | Grinder 2 Extract Fan-Motor
C8124_RV01_MO01 | EC02 | Grinder 1 Rotary Valve-Motor
C8124_SCW01_MO01 | T13 | Grinder 1 Discharge Screw-Motor
C8124_RV02_MO01 | EC03 | Grinder 2 Rotary Valve-Motor
C8124_SCW02_MO01 | T14 | Grinder 2 Discharge Screw-Motor
C8130_FA01_MO01 | VE07 | Weigh Bin Extract Fan-Motor
C8130_SCW31_MO01 | EX7 | Dosing Screw Silo 31-Motor
C8130_SCW32_MO01 | EX8 | Dosing Screw Silo 32-Motor
C8130_SCW33_MO01 | EX9 | Dosing Screw Silo 33-Motor
C8130_SCW34_MO01 | EX10 | Dosing Screw Silo 34-Motor
C8140_SB55_MO01 | DE55 | Scraper Bottom Silo 55-Motor
C8140_SCW55_MO01 | EX55 | Dosing Screw Silo 55-Motor
C8140_SB56_MO01 | DE56 | Scraper Bottom Silo 56-Motor
C8140_SCW56_MO01 | EX56 | Dosing Screw Silo 56-Motor
C8140_SB57_MO01 | DE57 | Scraper Bottom Silo 57-Motor
C8140_SCW57_MO01 | EX57 | Dosing Screw Silo 57-Motor
C8140_SB58_MO01 | DE58 | Scraper Bottom Silo 58-Motor
C8140_SCW58_MO01 | EX58 | Dosing Screw Silo 58-Motor
C8140_SB59_MO01 | DE59 | Scraper Bottom Silo 59-Motor
C8140_SCW59_MO01 | EX59 | Dosing Screw Silo 59-Motor
C8140_SB60_MO01 | DE60 | Scraper Bottom Silo 60-Motor
C8140_SCW60_MO01 | EX60 | Dosing Screw Silo 60-Motor
C8140_SCW61_MO01 | EX61 | Dosing Screw Silo 61-Motor
C8140_SCW62_MO01 | EX62 | Dosing Screw Silo 62-Motor
C8140_SCW63_MO01 | EX63 | Dosing Screw Silo 63-Motor
C8140_SCW64_MO01 | EX64 | Dosing Screw Silo 64-Motor
C8140_SCW65_MO01 | EX65 | Dosing Screw Silo 65-Motor
C8140_SCW66_MO01 | EX66 | Dosing Screw Silo 66-Motor
C8140_SCW67_MO01 | EX67 | Dosing Screw Silo 67-Motor
C8140_SCW68_MO01 | EX68 | Dosing Screw Silo 68-Motor
C8142_HM01_SV02 |  | Hammer on Micro Scale 1-Solenoid Valve
C8142_MX01_MO01 | M08 | Micro Mixer-Motor
C8150_FA01_MO01 | VS02 | Main Mixer Aspiration Fan-Motor
C8150_FI01_SV02 | FI25 | Main Mixer Filter-Solenoid Valve
C8150_MX01_MO01 | M03 | Main Mixer-Motor
C8150_CN01_MO01 | T15 | Main Mixer Conveyor-Motor
C8152_EV01_MO01 | E05 | Mixer Elevator-Start | 1 | [21 empty] | 4 MGs
C8152_FA01_MO01 | FE5 | Mixer Elevator Aspiration Fan-Motor
C8152_DB01_MO01 | DI04 | Distributor - Extruder Pre-Bins-Motor
C8210_FA01_MO01 | FI51 | Exturder Pre-Bin 1 Aspiration Fan-Motor
C8210_FI01_SV02 | FI51 | Exturder Pre-Bin 1 Filter-Solenoid Valve
C8210_FA02_MO01 | FI52 | Exturder Pre-Bin 2 Aspiration Fan-Motor
C8210_FI02_SV02 | FI52 | Exturder Pre-Bin 2 Filter-Solenoid Valve
C8210_SCW01_MO01 | EX41 | Discharge Screw Extruder Pre-Bin 1-Motor
C8210_SCW02_MO01 | EX42 | Discharge Screw Extruder Pre-Bin 2-Motor
C8210_SCW05_MO01 | T08 | Discharge Screw Extruder Pre-Bins-Motor
C8210_SI01_MO01 | TA14 | Exturder Sifter 1-Motor
C8210_SI02_MO01 | TA15 | Exturder Sifter 2-Motor
C8210_SCW06_MO01 | T22 | Sifter Discharge Screw Extruder-Motor
C8210_FA05_MO01 | VE29 | Loss-in-Weight Buffer Tank Fan-Motor
C8210_CN01_MO01 | T26 | Conveyor to LIW-Motor
C8210_FA06_MO01 | VE30 | Aspiration Fan LIW Conveyor-Motor
C8210_FA07_MO01 | VE31 | Aspiration Fan LIW Tank-Motor
C8210_LIW01_DO01 | TR07 | Loss-in-Weight System-Jesma Controller
C8210_LIW01_DO02 | TR07 | Loss-in-Weight System-Jesma Controller
C8210_SB01_MO01 | VF01 | LIW Tank Scarper Bottom-Motor
C8210_SCW07_MO01 | T27 | LIW Feed Screw-MOTOR
C8220_MX01_MO01 | COND01 | Pre-Conditioner 1-Motor
C8220_MX02_MO01 | COND02 | Pre-Conditioner 2-Motor
C8220_EXT01_MO01 | M04 | Extruder-Motor | [9 empty] | 1 | [12 empty] | 2 Safety Systems
C8220_FA01_MO01 | VE72 | Extruder Forced Ventilation-Motor
C8220_FA02_MO01 |  | Extruder Motor VSD Ventilation-Motor
C8220_HE01_DO01 | R02 | Extruder Heating-Elements
C8220_HY01_PU01_MO01 | M17 | Extruder Hydraulic Pump-Motor
C8220_PU01_MO01 | M02 | Extruder Lubrication Pump-Motor | [6 empty] | 1 | [15 empty] | 2 TTs
C8220_PU02_MO01 | M12 | Extruder Lubrication Pump Reduced-Motor
C8220_DZ01_MO01 | DEG | Degasser-Motor
C8220_CU01_MO01 | GRA01 | Extruder Cutter-Motor
C8224_FA01_MO01 | VE23 | Extruder Flash-Off Fan-Motor
C8224_RV01_MO01 | EC23 | Extruder Flash-Off Rotary Valve-Motor
C8226_CN01_MO01 | T51 | Extruder Conveyor-Motor
C8228_EV01_MO01 | E18 | Extruder Elevator-Motor
C8232_VB01_MO01 | AV01 | Vibro Conveyor after Dryer-Motor
C8232_VB01_MO02 | AV01 | Vibro Conveyor after Dryer-Motor
C8232_EV01_MO01 | E12 | Elevator after Dryer-Motor
C8232_FA01_MO01 | VE32 | Elevator Aspiration Fan-Motor
C8234_SI01_MO01 | TA09 | Coater Sifter-Motor
C8234_CN01_MO01 | T40 | Conveyor to Coater Pre-Bin-Motor
C8234_FA01_MO01 | VE70 | Vacuum Coater Aspiration Fan-Motor
C8234_SCW01_MO01 | T61 | Screw Conveyor to Waste-Motor
C8235_PU01_MO01 | PO11 | Fish Oil Dosing Pump-Motor
C8235_PU02_MO01 | PO47 | Veg Oil Dosing Pump-Motor
C8235_PU03_MO01 | PO38 | Oil Trimmings Dosing Pump-Motor
C8236_PU01_MO01 | PO49 | Coater Fat Sealant Pump-Motor
C8236_PU02_MO01 | PO39 | Coater Biol Pump-Motor
C8236_VC01_MX01_MO01 | M07 | Vacuum Coater Mixer-Motor
C8236_VP01_MO01 | PO41 | Vacuum Pump 1-Motor
C8236_VP02_MO01 | PO42 | Vacuum Pump 2-Motor
C8238_VB01_MO01 | AV02 | Coater Discharge Vibro-Motor
C8238_VB01_MO02 | AV02 | Coater Discharge Vibro-Motor
C8238_EV01_MO01 | E17 | Elevator after Coater-Motor
C8243_VB01_MO01 | AV03 | Cooler Discharge Vibro-Motor
C8243_VB01_MO02 | AV03 | Cooler Discharge Vibro-Motor
C8243_EV01_MO01 | E21 | Elevator after Cooler-Motor
C8243_EV02_MO01 | E42 | Elevator to MVS-Motor
C8250_DV01_LP01 | BD05 | Diverter After MVS-Lamp
C8250_DV01_LP02 | BD05 | Diverter After MVS-Lamp
C8250_VB01_MO01 | AV04 | Packing Vibro Feeder-Motor 1 | [8 empty] | 1 | [13 empty] | 2 PFs
C8250_VB01_MO02 | AV04 | Packing Vibro Feeder-Motor 2 | [8 empty] | 1 | [13 empty] | 2 PFs
C8250_SI01_MO01 | TA03 | Finished Product Sifter-Motor Left
C8250_SI01_MO02 | TA03 | Finished Product Sifter-Motor Right
C8251_EV01_MO01 | E08 | Elevator after MVS-Motor
C8251_DB01_MO01 | DI07 | Semi-Finished Product Distributor-Start
C8252_CN01_MO01 | T20 | Conveyor to Packing Lines-Motor
C8252_EV01_MO01 | E22 | Elevator from Packing Silos-Start
C8259_MVS01_MO01 |  | MVS Sprayer-Motor
C8259_MVS02_MO01 |  | MVS Spray Cylinder-Motor
C8259_BL01_MO01 |  | MVS Blower-Motor
C8259_PU01_MO01 | 1DP1 | MVS Dosing Pump-Motor
C8259_PU02_MO01 | 7VP1 | MVS Cold Oil Pump-Motor
C8259_PU03_MO01 | PO06 | MVS Oil Refill Pump-Motor
C8259_PU04_MO01 | 15EPV5 | MVS Enzyme Dosing Pump-Motor
C8259_PU05_MO01 |  | MVS Enzyme Dosing Pump-Motor
C8259_CH01_DO01 |  | MVS Cooling System-Chillers
C8259_SCW01_MO01 |  | MVS Solid Feeder-Motor
C8260_CN01_MO01 | T28 | Conveyor to Big Bag Packing-Start
C8260_LF01_MO01 |  | Hoist for Big Bags-Start
C8260_FA01_MO01 | VE02 | Extract Fan - Big Bag-Start
C8260_BE01_MO01 | T29 | Conveyor after Big Bag Weighing-
C8270_DE01_MO01 | EX50 | Fines Recovery Disc Elevator-Motor
C8270_SCW01_MO01 | EX45 | Rework Dosing Screw-Motor
C8822_CN01_MO01 | T19 | Conveyor to Crumbler-Start
C8822_SCW01_MO01 | CY03 | Feed Screw-Crumbler
C8822_CM01_MO01 | CY03 | Pellet Crumbler-Crumbler
C8822_CM01_MO02 | CY03 | Pellet Crumbler-Gap Adjustment Right
C8822_CM01_MO03 | CY03 | Pellet Crumbler-Gap Adjustment Left
C8828_SI01_MO01 | TA21 | Sifter After Crumbler-
C8828_DE01_MO01 | T76 | Disc Elevator Crumbling-
C8828_SCW01_MO01 | T77 | Screw Conveyor 1 Crumbling-
C8828_SI02_MO01 | TA22 | Final Sifter-
C8828_FA01_MO01 | EC40 | Aspiration Fan-
C8828_FI01_MO01 | FI40 | Bagging Filter-
C8833_RV01_MO01 | APIA | Rotary Valve-Motor
C8833_SCW01_MO01 | APIA | Transport Screw-Motor
C8835_TA01_MX01_MO01 | - | Liquid Tank Mixer-Crumbler
C8835_PU01_MO01 | - | Pump-Crumbler
C8836_MX01_MO01 | M06 | Micro Addition Mixer-Crumbler
C8838_VB01_MO01 | AV21 | Vibro Feeder to Bucket Packer-Motor
C8838_EV01_MO01 | E74 | Elevator to Bucket Packer-Motor
C3301_PU01_MO01 | PO26 | Process Water Pump PreCon-Motor
C3301_PU02_MO01 | PO13 | Process Water Pump Extruder-Motor
C3801_PU01_MO01 | PO01 | Oil Pump to Day Tank 3-Motor
C3801_PU02_MO01 | PO02 | Oil Pump to Day Tank 2-Motor
C3801_PU03_MO01 | PO03 | Oil Pump to Day Tank 1-Motor
C3802_TA01_MX01_MO01 | AG5.1 | Day Tank 1 Mixer-Motor
C3802_TA02_MX01_MO01 | AG02 | Day Tank 2 Mixer-Motor
C3802_TA03_MX01_MO01 | AG03 | Day Tank 3 Mixer-Motor
C3810_PU01_MO01 | PO13 | Oil Pump to Fat Sealant Buffer Tank-Motor
C3810_PU02_MO01 | PO46 | Fat Sealant Circulation Pump-Motor
C3810_SO01_VB01 |  | Fat Sealant Flakes Silo-Vibro
C3810_EV01_MO01 |  | Fat Sealant Flakes Elevator-Motor
C3810_HE01_XX01 |  | Fat Sealant Heater-Stage 1
C3810_HE01_XX02 |  | Fat Sealant Heater-Stage 2
C3810_HE01_XX03 |  | Fat Sealant Heater-Stage 3
C3810_HE01_XX04 |  | Fat Sealant Heater-Stage 4
C3810_HE01_XX05 |  | Fat Sealant Heater-Stage 5
C3810_TA02_MX01_MO01 |  | Fat Sealant Tank Mixer-Motor
C3810_TA02_HE01_XX01 |  | Fat Sealant Mixer Tank Heater-Stage 1
C3810_TA02_HE01_XX02 |  | Fat Sealant Mixer Tank Heater-Stage 2
C3820_PU01_MO01 | PO27 | Spare Oil Pump-Motor
C3820_PU02_MO01 | PO48 | Oil Pump to Extruder-Motor
C3851_HE01_DO01 | L1.04 | Liquid Additive 1 Room Heater-Heating Controls
C3851_HE02_DO01 | L1.08 | Liquid Additive 1 Hose Heater-Heating Controls
C3851_HE03_DO01 | L1.13 | Liquid Additive 1 Pipe Heater-Heating Controls
C3851_PU01_MO01 | L1.02 | Liquid Additive 1 Pump-Motor

## Alarm Function Enabled
Tag | Old Tag | Description | XMG - Misalignment Guard | XOS - Overflow Switch | XRG - Rotation Guard | XFS - Flow Switch | XEX - Explosion Signal | XDWN - Downstream Signal | XTT - Temperature | XDS - Door Switch | XPF - Power Fault | XSS - Safety System | XIS - Isolator Fault | XMCB - Circuit Breaker Fault | XTH - Thermistor | XLS - Level Switch | XINT1 - Undefined | XINT2 - Undefined | XINT3 - Undefined | XINT4 - Undefined | XINT5 - Undefined | XINT6 - Undefined | XINT7 - Undefined | XINT8 - Undefined | PF Comments | MCB Comments | XINT1 Comment | XINT2 Comment | XINT3 Comment | Rev | Rev Comment
C8010_FA01_MO01 | VE13 | Bulk Intake Pit Extract Fan 1-Motor | [11 empty] | 1
C8010_FI01_DO01 | FI13 | Bulk Intake Pit Filter 1-Start Command
C8010_FA02_MO01 | VE14 | Bulk Intake Pit Extract Fan 2-Motor | [11 empty] | 1
C8010_FI02_DO01 | FI14 | Bulk Intake Pit Filter 2-Start Command
C8010_FA03_MO01 | VE15 | Bulk Intake Pit Extract Fan 3-Motor | [11 empty] | 1
C8010_FI03_DO01 | FI15 | Bulk Intake Pit Filter 3-Start Command
C8010_SCW01_MO01 | T01 | Bulk Intake Screw Conveyor 1-Motor |  | 1 | [9 empty] | 1
C8010_EV01_MO01 | E01 | Bulk Intake Elevator 1-Start | 1 |  | 1 | [8 empty] | 1
C8010_FA04_MO01 | VE18 | Bulk Intake Elevator 1 Fan-Motor | [11 empty] | 1
C8010_SCW02_MO01 | T02 | Bulk Intake Screw Conveyor 2-Motor |  | 1 | [9 empty] | 1
C8010_EV02_MO01 | E02 | Bulk Intake Elevator 2-Start | 1 |  | 1 | [8 empty] | 1
C8010_FA05_MO01 | VE19 | Bulk Intake Elevator 2 Fan-Motor | [11 empty] | 1
C8020_SCW01_MO01 | T03 | Silo Top Screw Conveyor 1-Motor |  | 1 | [9 empty] | 1
C8020_FA01_MO01 | VE20 | Silo Top Screw Conveyor 1 Fan-Motor | [11 empty] | 1
C8020_FI01_DO01 | FI20 | Silo Top Conveyor 1 Filter-Start Command
C8020_SCW02_MO01 | T04 | Silo Top Screw Conveyor 2-Motor |  | 1 | [9 empty] | 1
C8020_FA02_MO01 | VE21 | Silo Top Screw Conveyor 2 Fan-Motor | [11 empty] | 1
C8020_FI02_DO01 | FI21 | Silo Top Conveyor 2 Filter-Start Command
C8020_DB01_MO01 | RT04 | Silo Top Rotating Distributor-Motor | [11 empty] | 1 |  |  | 1 | 1 | [8 empty] | Endstop Right | Endstop Left
C8020_FI03_DO01 | FI33 | Bulk Silo 1 Filter-Start Command
C8020_FI04_DO01 | FI34 | Bulk Silo 4 Filter-Start Command
C8020_FA09_MO01 | VE31 | Bulk Silo 13 Fan-Motor | [11 empty] | 1
C8020_FI09_DO01 | FI31 | Bulk Silo 13 Filter-Start Command
C8020_FA07_MO01 | VE42 | Bulk Silo 15 Fan-Motor | [11 empty] | 1
C8020_FI07_DO01 | FI42 | Bulk Silo 15 Filter-Start Command
C8020_FA08_MO01 | VE41 | Bulk Silo 16 Fan-Motor | [11 empty] | 1
C8020_FI08_DO01 | FI41 | Bulk Silo 16 Filter-Start Command
C8020_FA10_MO01 | VE16 | Bulk Silo 23-25 Fan 1-Motor | [11 empty] | 1
C8020_FA11_MO01 | VE17 | Bulk Silo 23-25 Fan 2-Motor | [11 empty] | 1
C8020_CN01_MO01 | T65 | Silo Top Chain Conveyor 1-Motor |  | 1 | [9 empty] | 1
C8020_FI05_DO01 | FI35 | Bulk Silo 7 Filter-Start Command
C8020_FI06_DO01 | FI36 | Bulk Silo 8 Filter-Start Command
C8040_FA01_MO01 | VE20 | Micro Dosing Room Extract Fan-Motor | [11 empty] | 1
C8040_FI01_DO01 | FI20 | Micro Dosing Filter-Start Command
C8040_LF01_MO01 | HOIST | Hoist at Top of Micro Silos-Motor Up/Down | [10 empty] | 1 | 1
C8040_LF01_MO02 | HOIST | Hoist at Top of Micro Silos-Motor Left/Right | [10 empty] | 1 | 1
C8040_LF01_MO03 | HOIST | Hoist at Top of Micro Silos-Motor Forward/Back | [10 empty] | 1 | 1
C8040_LF01_PB01_DO01 | HOIST | Level 0 Hoist Command-Level 0 Lamp Indication
C8040_LF01_PB02_DO02 | HOIST | Level 2 Hoist Command-Level 2 Lamp Indication
C8110_SCW01_MO01 | EX1 | Dosing Screw Silo 1-Motor | [8 empty] | 1 | [13 empty] | Tripped Breaker on VSD |  | Scale Comms
C8110_SCW02_MO01 | EX2 | Dosing Screw Silo 2-Motor | [8 empty] | 1 | [13 empty] | Tripped Breaker on VSD |  | Scale Comms
C8110_SCW03_MO01 | EX3 | Dosing Screw Silo 3-Motor | [8 empty] | 1 | [13 empty] | Tripped Breaker on VSD |  | Scale Comms
C8110_SCW04_MO01 | EX4 | Dosing Screw Silo 4-Motor | [8 empty] | 1 | [13 empty] | Tripped Breaker on VSD |  | Scale Comms
C8110_SCW05_MO01 | EX5 | Dosing Screw Silo 5-Motor | [8 empty] | 1 | [13 empty] | Tripped Breaker on VSD |  | Scale Comms
C8110_SCW06_MO01 | EX6 | Dosing Screw Silo 6-Motor | [8 empty] | 1 | [13 empty] | Tripped Breaker on VSD |  | Scale Comms
C8110_SCW07_MO01 | EX7 | Dosing Screw Silo 7-Motor | [8 empty] | 1 | [13 empty] | Tripped Breaker on VSD |  | Scale Comms
C8110_SCW08_MO01 | EX8 | Dosing Screw Silo 8-Motor | [8 empty] | 1 | [13 empty] | Tripped Breaker on VSD |  | Scale Comms
C8110_SCW09_MO01 | EX9 | Dosing Screw Silo 9-Motor | [8 empty] | 1 | [13 empty] | Tripped Breaker on VSD |  | Scale Comms
C8110_VB09_MO01 | EX9 | Dosing Vibro Silo 9-Motor
C8110_VB09_MO02 | EX9 | Dosing Vibro Silo 9-Motor
C8110_SCW10_MO01 | EX10 | Dosing Screw Silo 10-Motor | [8 empty] | 1 | [13 empty] | Tripped Breaker on VSD |  | Scale Comms
C8110_VB10_MO01 | EX10 | Dosing Vibro Silo 10-Motor
C8110_VB10_MO02 | EX10 | Dosing Vibro Silo 10-Motor
C8110_SCW13_MO01 | EX13 | Dosing Screw Silo 13-Motor | [8 empty] | 1 | [13 empty] | Tripped Breaker on VSD |  | Scale Comms
C8110_SCW14_MO01 | EX14 | Dosing Screw Silo 14-Motor | [8 empty] | 1 | [13 empty] | Tripped Breaker on VSD |  | Scale Comms
C8110_SCW15_MO01 | EX15 | Dosing Screw Silo 15-Motor | [8 empty] | 1 | [13 empty] | Tripped Breaker on VSD |  | Scale Comms
C8110_SCW16_MO01 | EX16 | Dosing Screw Silo 16-Motor | [8 empty] | 1 | [13 empty] | Tripped Breaker on VSD |  | Scale Comms
C8110_VB16_MO01 | EX16 | Dosing Vibro Silo 16-Motor
C8110_VB16_MO02 | EX16 | Dosing Vibro Silo 16-Motor
C8110_SCW17_MO01 | EX17 | Dosing Screw Silo 17-Motor | [8 empty] | 1 | [13 empty] | Tripped Breaker on VSD |  | Scale Comms
C8110_SCW18_MO01 | EX18 | Dosing Screw Silo 18-Motor | [8 empty] | 1 | [13 empty] | Tripped Breaker on VSD |  | Scale Comms
C8110_SCW19_MO01 | EX19 | Dosing Screw Silo 19-Motor | [8 empty] | 1 | [13 empty] | Tripped Breaker on VSD |  | Scale Comms
C8110_VB19_MO01 | EX19 | Dosing Vibro Silo 19-Motor
C8110_VB19_MO02 | EX19 | Dosing Vibro Silo 19-Motor
C8110_SCW20_MO01 | EX20 | Dosing Screw Silo 20-Motor | [8 empty] | 1 | [13 empty] | Tripped Breaker on VSD |  | Scale Comms
C8110_SCW23_MO01 | EX23 | Dosing Screw Silo 23-Motor | [8 empty] | 1 | [13 empty] | Tripped Breaker on VSD |  | Scale Comms
C8110_SCW24_MO01 | EX24 | Dosing Screw Silo 24-Motor | [8 empty] | 1 | [13 empty] | Tripped Breaker on VSD |  | Scale Comms
C8110_SCW25_MO01 | EX25 | Dosing Screw Silo 25-Motor | [8 empty] | 1 | [13 empty] | Tripped Breaker on VSD |  | Scale Comms
C8112_CN01_MO01 | T09 | Primary Dosing Scale Discharge Conveyor-Motor |  | 1
C8112_FA01_MO01 | FT09 | Scale Discharge Conveyor Aspiration Fan-Motor
C8114_CN01_MO01 | T10 | Batch Transport Conveyor 1-Motor |  | 1
C8114_FA01_MO01 | FT10 | Batch Transport Conveyor Aspiration Fan-Motor
C8114_EV01_MO01 | E03 | Batch Transport Elevator 1-Start | 1 |  | 1
C8114_FA02_MO01 | FE3 | Batch Transport Elevator Aspiration Fan-Motor
C8120_MX01_MO01 | M02 | Pre-Mixer-Motor
C8122_SCW01_MO01 | AL01 | Grinder 1 Feed Screw-Motor |  | 1 |  |  |  |  | 1 |  |  |  |  | 1 | [11 empty] | From VSD
C8122_SCW01_MO02 | AL01 | Grinder 1 Feed Screw-Forced Ventilation Motor | [11 empty] | 1
C8122_CR01_MO01 | PB01 | Grinder 1 Lump Crusher-Motor |  |  | 1 |  |  |  | 1 |  | 1 |  |  | 1 | [10 empty] | Soft Starter Fault
C8122_ML01_MO01 | BR01 | Grinder 1-Motor | [6 empty] | 1 | 1 | 1 | 1 |  | 1
C8122_ML01_SS02_LP01 | KA180 | Grinder 1 Door Safety System-Indication Lamp
C8122_FA01_MO01 | VE03 | Grinder 1 Extract Fan-Motor | [8 empty] | 1 |  |  | 1 | [10 empty] | VSD Fault
C8122_SCW02_MO01 | AL02 | Grinder 2 Feed Screw-Motor |  | 1 |  |  |  |  | 1 |  |  |  |  | 1 | [11 empty] | From VSD
C8122_SCW02_MO02 | AL02 | Grinder 1 Feed Screw-Forced Ventilation Motor | [11 empty] | 1
C8122_CR02_MO01 | PB02 | Grinder 2 Lump Crusher-Motor |  |  | 1 |  |  |  | 1 |  | 1 |  |  | 1 | [10 empty] | Soft Starter Fault
C8122_ML02_MO01 | BR02 | Grinder 2-Motor | [6 empty] | 1 | 1 | 1 | 1 |  | 1
C8122_ML02_SS02_LP01 | KA180 | Grinder 2 Door Safety System-Indication Lamp
C8122_FA02_MO01 | VE04 | Grinder 2 Extract Fan-Motor | [8 empty] | 1 |  |  | 1 | [10 empty] | VSD Fault
C8124_RV01_MO01 | EC02 | Grinder 1 Rotary Valve-Motor
C8124_SCW01_MO01 | T13 | Grinder 1 Discharge Screw-Motor |  | 1
C8124_RV02_MO01 | EC03 | Grinder 2 Rotary Valve-Motor
C8124_SCW02_MO01 | T14 | Grinder 2 Discharge Screw-Motor |  | 1
C8130_FA01_MO01 | VE07 | Weigh Bin Extract Fan-Motor
C8130_SCW31_MO01 | EX7 | Dosing Screw Silo 31-Motor | [8 empty] | 1 | [13 empty] | Tripped Breaker on VSD |  | Scale Comms
C8130_SCW32_MO01 | EX8 | Dosing Screw Silo 32-Motor | [8 empty] | 1 | [13 empty] | Tripped Breaker on VSD |  | Scale Comms
C8130_SCW33_MO01 | EX9 | Dosing Screw Silo 33-Motor | [8 empty] | 1 | [13 empty] | Tripped Breaker on VSD |  | Scale Comms
C8130_SCW34_MO01 | EX10 | Dosing Screw Silo 34-Motor | [8 empty] | 1 | [13 empty] | Tripped Breaker on VSD |  | Scale Comms
C8140_SB55_MO01 | DE55 | Scraper Bottom Silo 55-Motor | [10 empty] | 1 | 1
C8140_SCW55_MO01 | EX55 | Dosing Screw Silo 55-Motor | [8 empty] | 1 |  | 1 | [11 empty] | Tripped Breaker on VSD |  | Scale Comms
C8140_SB56_MO01 | DE56 | Scraper Bottom Silo 56-Motor | [10 empty] | 1 | 1
C8140_SCW56_MO01 | EX56 | Dosing Screw Silo 56-Motor | [8 empty] | 1 |  | 1 | [11 empty] | Tripped Breaker on VSD |  | Scale Comms
C8140_SB57_MO01 | DE57 | Scraper Bottom Silo 57-Motor | [10 empty] | 1 | 1
C8140_SCW57_MO01 | EX57 | Dosing Screw Silo 57-Motor | [8 empty] | 1 |  | 1 | [11 empty] | Tripped Breaker on VSD |  | Scale Comms
C8140_SB58_MO01 | DE58 | Scraper Bottom Silo 58-Motor | [10 empty] | 1 | 1
C8140_SCW58_MO01 | EX58 | Dosing Screw Silo 58-Motor | [8 empty] | 1 |  | 1 | [11 empty] | Tripped Breaker on VSD |  | Scale Comms
C8140_SB59_MO01 | DE59 | Scraper Bottom Silo 59-Motor | [10 empty] | 1 | 1
C8140_SCW59_MO01 | EX59 | Dosing Screw Silo 59-Motor | [8 empty] | 1 |  | 1 | [11 empty] | Tripped Breaker on VSD |  | Scale Comms
C8140_SB60_MO01 | DE60 | Scraper Bottom Silo 60-Motor | [10 empty] | 1 | 1
C8140_SCW60_MO01 | EX60 | Dosing Screw Silo 60-Motor | [8 empty] | 1 |  | 1 | [11 empty] | Tripped Breaker on VSD |  | Scale Comms
C8140_SCW61_MO01 | EX61 | Dosing Screw Silo 61-Motor | [8 empty] | 1 |  | 1 | [11 empty] | Tripped Breaker on VSD |  | Scale Comms
C8140_SCW62_MO01 | EX62 | Dosing Screw Silo 62-Motor | [8 empty] | 1 |  | 1 | [11 empty] | Tripped Breaker on VSD |  | Scale Comms
C8140_SCW63_MO01 | EX63 | Dosing Screw Silo 63-Motor | [8 empty] | 1 |  | 1 | [11 empty] | Tripped Breaker on VSD |  | Scale Comms
C8140_SCW64_MO01 | EX64 | Dosing Screw Silo 64-Motor | [8 empty] | 1 |  | 1 | [11 empty] | Tripped Breaker on VSD |  | Scale Comms
C8140_SCW65_MO01 | EX65 | Dosing Screw Silo 65-Motor | [8 empty] | 1 |  | 1 | [11 empty] | Tripped Breaker on VSD |  | Scale Comms
C8140_SCW66_MO01 | EX66 | Dosing Screw Silo 66-Motor | [8 empty] | 1 |  | 1 | [11 empty] | Tripped Breaker on VSD |  | Scale Comms
C8140_SCW67_MO01 | EX67 | Dosing Screw Silo 67-Motor | [8 empty] | 1 |  | 1 | [11 empty] | Tripped Breaker on VSD |  | Scale Comms
C8140_SCW68_MO01 | EX68 | Dosing Screw Silo 68-Motor | [8 empty] | 1 |  | 1 | [11 empty] | Tripped Breaker on VSD |  | Scale Comms
C8142_HM01_SV02 |  | Hammer on Micro Scale 1-Solenoid Valve
C8142_MX01_MO01 | M08 | Micro Mixer-Motor | [10 empty] | 1 | 1
C8150_FA01_MO01 | VS02 | Main Mixer Aspiration Fan-Motor
C8150_FI01_SV02 | FI25 | Main Mixer Filter-Solenoid Valve
C8150_MX01_MO01 | M03 | Main Mixer-Motor | [6 empty] | 1 | [5 empty] | 1
C8150_CN01_MO01 | T15 | Main Mixer Conveyor-Motor |  | 1
C8152_EV01_MO01 | E05 | Mixer Elevator-Start | 1 |  | 1
C8152_FA01_MO01 | FE5 | Mixer Elevator Aspiration Fan-Motor
C8152_DB01_MO01 | DI04 | Distributor - Extruder Pre-Bins-Motor
C8210_FA01_MO01 | FI51 | Exturder Pre-Bin 1 Aspiration Fan-Motor
C8210_FI01_SV02 | FI51 | Exturder Pre-Bin 1 Filter-Solenoid Valve
C8210_FA02_MO01 | FI52 | Exturder Pre-Bin 2 Aspiration Fan-Motor
C8210_FI02_SV02 | FI52 | Exturder Pre-Bin 2 Filter-Solenoid Valve
C8210_SCW01_MO01 | EX41 | Discharge Screw Extruder Pre-Bin 1-Motor |  | 1 | [6 empty] | 1 | [13 empty] | Tripped Breaker on VSD
C8210_SCW02_MO01 | EX42 | Discharge Screw Extruder Pre-Bin 2-Motor |  | 1 | [6 empty] | 1 | [13 empty] | Tripped Breaker on VSD
C8210_SCW05_MO01 | T08 | Discharge Screw Extruder Pre-Bins-Motor |  | 1
C8210_SI01_MO01 | TA14 | Exturder Sifter 1-Motor
C8210_SI02_MO01 | TA15 | Exturder Sifter 2-Motor
C8210_SCW06_MO01 | T22 | Sifter Discharge Screw Extruder-Motor |  | 1 | [22 empty] | Magnet Door Open
C8210_FA05_MO01 | VE29 | Loss-in-Weight Buffer Tank Fan-Motor
C8210_CN01_MO01 | T26 | Conveyor to LIW-Motor |  | 1 | [22 empty] | Scale Comms
C8210_FA06_MO01 | VE30 | Aspiration Fan LIW Conveyor-Motor
C8210_FA07_MO01 | VE31 | Aspiration Fan LIW Tank-Motor
C8210_LIW01_DO01 | TR07 | Loss-in-Weight System-Jesma Controller
C8210_LIW01_DO02 | TR07 | Loss-in-Weight System-Jesma Controller
C8210_SB01_MO01 | VF01 | LIW Tank Scarper Bottom-Motor
C8210_SCW07_MO01 | T27 | LIW Feed Screw-MOTOR | [6 empty] | 1 |  |  |  |  | 1
C8220_MX01_MO01 | COND01 | Pre-Conditioner 1-Motor |  |  | 1 |  |  |  |  | 1
C8220_MX02_MO01 | COND02 | Pre-Conditioner 2-Motor | [8 empty] | 1
C8220_EXT01_MO01 | M04 | Extruder-Motor |  |  | 1 |  |  |  | 1 |  | 1 | 1 |  | 1 |  |  | 1 | 1 | 1 | [5 empty] | VSD Fault |  | Brush Fault | Motor Housing Open | Torque Limiter
C8220_FA01_MO01 | VE72 | Extruder Forced Ventilation-Motor | [6 empty] | 1 |  |  |  |  | 1 |  |  | 1 | [9 empty] | Pressure Switch
C8220_FA02_MO01 |  | Extruder Motor VSD Ventilation-Motor | [11 empty] | 1
C8220_HE01_DO01 | R02 | Extruder Heating-Elements
C8220_HY01_PU01_MO01 | M17 | Extruder Hydraulic Pump-Motor | [11 empty] | 1
C8220_PU01_MO01 | M02 | Extruder Lubrication Pump-Motor | [6 empty] | 1 |  |  |  |  | 1 |  |  | 1 | 1 | [8 empty] | Pressure Switch | Oil Filter Fault
C8220_PU02_MO01 | M12 | Extruder Lubrication Pump Reduced-Motor | [11 empty] | 1 |  |  | 1 | [9 empty] | Pressure Switch
C8220_DZ01_MO01 | DEG | Degasser-Motor | [8 empty] | 1 | [13 empty] | VSD Fault
C8220_CU01_MO01 | GRA01 | Extruder Cutter-Motor | [7 empty] | 1 | 1 | 1 |  | 1 | [10 empty] | VSD Fault
C8224_FA01_MO01 | VE23 | Extruder Flash-Off Fan-Motor
C8224_RV01_MO01 | EC23 | Extruder Flash-Off Rotary Valve-Motor
C8226_CN01_MO01 | T51 | Extruder Conveyor-Motor
C8228_EV01_MO01 | E18 | Extruder Elevator-Motor | [8 empty] | 1
C8232_VB01_MO01 | AV01 | Vibro Conveyor after Dryer-Motor | [11 empty] | 1
C8232_VB01_MO02 | AV01 | Vibro Conveyor after Dryer-Motor | [11 empty] | 1
C8232_EV01_MO01 | E12 | Elevator after Dryer-Motor |  |  | 1 | [8 empty] | 1
C8232_FA01_MO01 | VE32 | Elevator Aspiration Fan-Motor | [11 empty] | 1
C8234_SI01_MO01 | TA09 | Coater Sifter-Motor | [11 empty] | 1
C8234_CN01_MO01 | T40 | Conveyor to Coater Pre-Bin-Motor |  |  | 1 | [8 empty] | 1
C8234_FA01_MO01 | VE70 | Vacuum Coater Aspiration Fan-Motor | [11 empty] | 1
C8234_SCW01_MO01 | T61 | Screw Conveyor to Waste-Motor | [11 empty] | 1
C8235_PU01_MO01 | PO11 | Fish Oil Dosing Pump-Motor | [8 empty] | 1 |  |  | 1 | [10 empty] | VSD Fault
C8235_PU02_MO01 | PO47 | Veg Oil Dosing Pump-Motor | [8 empty] | 1 |  |  | 1
C8235_PU03_MO01 | PO38 | Oil Trimmings Dosing Pump-Motor | [8 empty] | 1 |  |  | 1
C8236_PU01_MO01 | PO49 | Coater Fat Sealant Pump-Motor | [8 empty] | 1 | [13 empty] | VSD Fault
C8236_PU02_MO01 | PO39 | Coater Biol Pump-Motor | [8 empty] | 1 | [13 empty] | VSD Fault
C8236_VC01_MX01_MO01 | M07 | Vacuum Coater Mixer-Motor | [8 empty] | 1 |  | 1 | 1 | [10 empty] | VSD Fault
C8236_VP01_MO01 | PO41 | Vacuum Pump 1-Motor | [10 empty] | 1 | 1
C8236_VP02_MO01 | PO42 | Vacuum Pump 2-Motor | [10 empty] | 1 | 1
C8238_VB01_MO01 | AV02 | Coater Discharge Vibro-Motor | [8 empty] | 1 |  |  | 1 | [10 empty] | Tripped Breaker for common supply
C8238_VB01_MO02 | AV02 | Coater Discharge Vibro-Motor | [8 empty] | 1 |  |  | 1 | [10 empty] | Tripped Breaker for common supply
C8238_EV01_MO01 | E17 | Elevator after Coater-Motor |  |  | 1 | [8 empty] | 1
C8243_VB01_MO01 | AV03 | Cooler Discharge Vibro-Motor | [8 empty] | 1 |  |  | 1 | [10 empty] | Tripped Breaker for common supply
C8243_VB01_MO02 | AV03 | Cooler Discharge Vibro-Motor | [8 empty] | 1 |  |  | 1 | [10 empty] | Tripped Breaker for common supply
C8243_EV01_MO01 | E21 | Elevator after Cooler-Motor |  |  | 1 | [8 empty] | 1
C8243_EV02_MO01 | E42 | Elevator to MVS-Motor |  |  | 1 | [8 empty] | 1 |  |  | 1 | [9 empty] | Pressure Switch
C8250_DV01_LP01 | BD05 | Diverter After MVS-Lamp
C8250_DV01_LP02 | BD05 | Diverter After MVS-Lamp
C8250_VB01_MO01 | AV04 | Packing Vibro Feeder-Motor 1 | [8 empty] | 1 |  |  | 1 | [10 empty] | Tripped Breaker for common supply AND Power On Signal
C8250_VB01_MO02 | AV04 | Packing Vibro Feeder-Motor 2 | [8 empty] | 1 |  |  | 1 | [10 empty] | Tripped Breaker for common supply AND Power On Signal
C8250_SI01_MO01 | TA03 | Finished Product Sifter-Motor Left | [10 empty] | 1 | 1 | [10 empty] | Pressure Switch
C8250_SI01_MO02 | TA03 | Finished Product Sifter-Motor Right | [10 empty] | 1 | 1 | [10 empty] | Pressure Switch
C8251_EV01_MO01 | E08 | Elevator after MVS-Motor |  | 1 | 1 | [8 empty] | 1
C8251_DB01_MO01 | DI07 | Semi-Finished Product Distributor-Start | [11 empty] | 1
C8252_CN01_MO01 | T20 | Conveyor to Packing Lines-Motor |  | 1
C8252_EV01_MO01 | E22 | Elevator from Packing Silos-Start |  |  | 1 |  |  |  |  | 1 |  |  |  | 1
C8259_MVS01_MO01 |  | MVS Sprayer-Motor |  |  | 1
C8259_MVS02_MO01 |  | MVS Spray Cylinder-Motor |  |  | 1
C8259_BL01_MO01 |  | MVS Blower-Motor | [11 empty] | 1
C8259_PU01_MO01 | 1DP1 | MVS Dosing Pump-Motor
C8259_PU02_MO01 | 7VP1 | MVS Cold Oil Pump-Motor
C8259_PU03_MO01 | PO06 | MVS Oil Refill Pump-Motor | [11 empty] | 1
C8259_PU04_MO01 | 15EPV5 | MVS Enzyme Dosing Pump-Motor
C8259_PU05_MO01 |  | MVS Enzyme Dosing Pump-Motor
C8259_CH01_DO01 |  | MVS Cooling System-Chillers
C8259_SCW01_MO01 |  | MVS Solid Feeder-Motor
C8260_CN01_MO01 | T28 | Conveyor to Big Bag Packing-Start |  | 1 | [8 empty] | 1 | 1
C8260_LF01_MO01 |  | Hoist for Big Bags-Start | [10 empty] | 1 | 1
C8260_FA01_MO01 | VE02 | Extract Fan - Big Bag-Start | [10 empty] | 1 | 1
C8260_BE01_MO01 | T29 | Conveyor after Big Bag Weighing-
C8270_DE01_MO01 | EX50 | Fines Recovery Disc Elevator-Motor |  |  | 1 | [21 empty] | Chainguard
C8270_SCW01_MO01 | EX45 | Rework Dosing Screw-Motor | [24 empty] | Scale Comms
C8822_CN01_MO01 | T19 | Conveyor to Crumbler-Start |  | 1 | [9 empty] | 1
C8822_SCW01_MO01 | CY03 | Feed Screw-Crumbler | [11 empty] | 1
C8822_CM01_MO01 | CY03 | Pellet Crumbler-Crumbler | [11 empty] | 1
C8822_CM01_MO02 | CY03 | Pellet Crumbler-Gap Adjustment Right | [11 empty] | 1
C8822_CM01_MO03 | CY03 | Pellet Crumbler-Gap Adjustment Left | [11 empty] | 1
C8828_SI01_MO01 | TA21 | Sifter After Crumbler- | [11 empty] | 1
C8828_DE01_MO01 | T76 | Disc Elevator Crumbling- | [11 empty] | 1
C8828_SCW01_MO01 | T77 | Screw Conveyor 1 Crumbling- | [11 empty] | 1
C8828_SI02_MO01 | TA22 | Final Sifter- | [11 empty] | 1
C8828_FA01_MO01 | EC40 | Aspiration Fan- | [11 empty] | 1
C8828_FI01_MO01 | FI40 | Bagging Filter- | [14 empty] | 1 | [9 empty] | Blocked
C8833_RV01_MO01 | APIA | Rotary Valve-Motor | [11 empty] | 1
C8833_SCW01_MO01 | APIA | Transport Screw-Motor | [11 empty] | 1
C8835_TA01_MX01_MO01 | - | Liquid Tank Mixer-Crumbler | [11 empty] | 1
C8835_PU01_MO01 | - | Pump-Crumbler | [11 empty] | 1
C8836_MX01_MO01 | M06 | Micro Addition Mixer-Crumbler | [7 empty] | 1 |  | 1 |  | 1
C8838_VB01_MO01 | AV21 | Vibro Feeder to Bucket Packer-Motor | [11 empty] | 1
C8838_EV01_MO01 | E74 | Elevator to Bucket Packer-Motor | [11 empty] | 1
C3301_PU01_MO01 | PO26 | Process Water Pump PreCon-Motor | [8 empty] | 1 | [13 empty] | VSD Fault
C3301_PU02_MO01 | PO13 | Process Water Pump Extruder-Motor | [8 empty] | 1
C3801_PU01_MO01 | PO01 | Oil Pump to Day Tank 3-Motor
C3801_PU02_MO01 | PO02 | Oil Pump to Day Tank 2-Motor
C3801_PU03_MO01 | PO03 | Oil Pump to Day Tank 1-Motor
C3802_TA01_MX01_MO01 | AG5.1 | Day Tank 1 Mixer-Motor | [11 empty] | 1
C3802_TA02_MX01_MO01 | AG02 | Day Tank 2 Mixer-Motor
C3802_TA03_MX01_MO01 | AG03 | Day Tank 3 Mixer-Motor
C3810_PU01_MO01 | PO13 | Oil Pump to Fat Sealant Buffer Tank-Motor | [8 empty] | 1 |  |  | 1 | [10 empty] | VSD Fault
C3810_PU02_MO01 | PO46 | Fat Sealant Circulation Pump-Motor | [8 empty] | 1 | [13 empty] | VSD Fault
C3810_SO01_VB01 |  | Fat Sealant Flakes Silo-Vibro
C3810_EV01_MO01 |  | Fat Sealant Flakes Elevator-Motor
C3810_HE01_XX01 |  | Fat Sealant Heater-Stage 1
C3810_HE01_XX02 |  | Fat Sealant Heater-Stage 2
C3810_HE01_XX03 |  | Fat Sealant Heater-Stage 3
C3810_HE01_XX04 |  | Fat Sealant Heater-Stage 4
C3810_HE01_XX05 |  | Fat Sealant Heater-Stage 5
C3810_TA02_MX01_MO01 |  | Fat Sealant Tank Mixer-Motor | [8 empty] | 1 | [13 empty] | VSD Fault
C3810_TA02_HE01_XX01 |  | Fat Sealant Mixer Tank Heater-Stage 1
C3810_TA02_HE01_XX02 |  | Fat Sealant Mixer Tank Heater-Stage 2
C3820_PU01_MO01 | PO27 | Spare Oil Pump-Motor | [8 empty] | 1 | [13 empty] | VSD Fault
C3820_PU02_MO01 | PO48 | Oil Pump to Extruder-Motor
C3851_HE01_DO01 | L1.04 | Liquid Additive 1 Room Heater-Heating Controls
C3851_HE02_DO01 | L1.08 | Liquid Additive 1 Hose Heater-Heating Controls
C3851_HE03_DO01 | L1.13 | Liquid Additive 1 Pipe Heater-Heating Controls
C3851_PU01_MO01 | L1.02 | Liquid Additive 1 Pump-Motor

## Requires Reset
Tag | Old Tag | Description | XMG - Misalignment Guard | XOS - Overflow Switch | XRG - Rotation Guard | XFS - Flow Switch | XEX - Explosion Signal | XDWN - Downstream Signal | XTT - Temperature | XDS - Door Switch | XPF - Power Fault | XSS - Safety System | XIS - Isolator Fault | XMCB - Circuit Breaker Fault | XTH - Thermistor | XLS - Level Switch | XINT1 - Undefined | XINT2 - Undefined | XINT3 - Undefined | XINT4 - Undefined | XINT5 - Undefined | XINT6 - Undefined | XINT7 - Undefined | XINT8 - Undefined | External Block Comments | XDWN | PF Comments | MCB Comments | XINT1 Comment | XINT2 Comment | XINT3 Comment
C8010_FA01_MO01 | VE13 | Bulk Intake Pit Extract Fan 1-Motor | [11 empty] | 1
C8010_FI01_DO01 | FI13 | Bulk Intake Pit Filter 1-Start Command
C8010_FA02_MO01 | VE14 | Bulk Intake Pit Extract Fan 2-Motor | [11 empty] | 1
C8010_FI02_DO01 | FI14 | Bulk Intake Pit Filter 2-Start Command
C8010_FA03_MO01 | VE15 | Bulk Intake Pit Extract Fan 3-Motor | [11 empty] | 1
C8010_FI03_DO01 | FI15 | Bulk Intake Pit Filter 3-Start Command
C8010_SCW01_MO01 | T01 | Bulk Intake Screw Conveyor 1-Motor |  | 1 | [9 empty] | 1 | [11 empty] | C8010_EV01_MO01
C8010_EV01_MO01 | E01 | Bulk Intake Elevator 1-Start | 1 |  | 1 | [8 empty] | 1 | [10 empty] | 4 MGs | C8010_SCW02_MO01
C8010_FA04_MO01 | VE18 | Bulk Intake Elevator 1 Fan-Motor | [11 empty] | 1
C8010_SCW02_MO01 | T02 | Bulk Intake Screw Conveyor 2-Motor |  | 1 | [9 empty] | 1 | [11 empty] | C8010_EV02_MO01
C8010_EV02_MO01 | E02 | Bulk Intake Elevator 2-Start | 1 |  | 1 | [8 empty] | 1 | [10 empty] | 4 MGs | C8020_SCW01_MO01 OR C8020_CN01_MO01 depending on position of C8020_DV01
C8010_FA05_MO01 | VE19 | Bulk Intake Elevator 2 Fan-Motor | [11 empty] | 1
C8020_SCW01_MO01 | T03 | Silo Top Screw Conveyor 1-Motor |  | 1 | [9 empty] | 1 | [11 empty] | C8020_SCW02_MO01
C8020_FA01_MO01 | VE20 | Silo Top Screw Conveyor 1 Fan-Motor | [11 empty] | 1
C8020_FI01_DO01 | FI20 | Silo Top Conveyor 1 Filter-Start Command
C8020_SCW02_MO01 | T04 | Silo Top Screw Conveyor 2-Motor |  | 1 | [9 empty] | 1 | [10 empty] | 2 Overflow Switches, one at each end | C8020_DP01_FB02 OR C8020_DP02_FB02 telescopic pipe extended AND C8020_SG0X_FB02 (X=Destination Silo)
C8020_FA02_MO01 | VE21 | Silo Top Screw Conveyor 2 Fan-Motor | [11 empty] | 1
C8020_FI02_DO01 | FI21 | Silo Top Conveyor 2 Filter-Start Command
C8020_DB01_MO01 | RT04 | Silo Top Rotating Distributor-Motor | [11 empty] | 1 |  |  | 1 | 1 | [10 empty] | Endstop Right | Endstop Left
C8020_FI03_DO01 | FI33 | Bulk Silo 1 Filter-Start Command
C8020_FI04_DO01 | FI34 | Bulk Silo 4 Filter-Start Command
C8020_FA09_MO01 | VE31 | Bulk Silo 13 Fan-Motor | [11 empty] | 1
C8020_FI09_DO01 | FI31 | Bulk Silo 13 Filter-Start Command
C8020_FA07_MO01 | VE42 | Bulk Silo 15 Fan-Motor | [11 empty] | 1
C8020_FI07_DO01 | FI42 | Bulk Silo 15 Filter-Start Command
C8020_FA08_MO01 | VE41 | Bulk Silo 16 Fan-Motor | [11 empty] | 1
C8020_FI08_DO01 | FI41 | Bulk Silo 16 Filter-Start Command
C8020_FA10_MO01 | VE16 | Bulk Silo 23-25 Fan 1-Motor | [11 empty] | 1
C8020_FA11_MO01 | VE17 | Bulk Silo 23-25 Fan 2-Motor | [11 empty] | 1
C8020_CN01_MO01 | T65 | Silo Top Chain Conveyor 1-Motor |  | 1 | [9 empty] | 1 | [11 empty] | C8020_BV07_FB02 OR C8020_BV08_FB02 depending on position of C8020_DV02
C8020_FI05_DO01 | FI35 | Bulk Silo 7 Filter-Start Command
C8020_FI06_DO01 | FI36 | Bulk Silo 8 Filter-Start Command
C8040_FA01_MO01 | VE20 | Micro Dosing Room Extract Fan-Motor | [11 empty] | 1
C8040_FI01_DO01 | FI20 | Micro Dosing Filter-Start Command
C8040_LF01_MO01 | HOIST | Hoist at Top of Micro Silos-Motor Up/Down | [10 empty] | 1 | 1
C8040_LF01_MO02 | HOIST | Hoist at Top of Micro Silos-Motor Left/Right | [10 empty] | 1 | 1
C8040_LF01_MO03 | HOIST | Hoist at Top of Micro Silos-Motor Forward/Back | [10 empty] | 1 | 1
C8040_LF01_PB01_DO01 | HOIST | Level 0 Hoist Command-Level 0 Lamp Indication
C8040_LF01_PB02_DO02 | HOIST | Level 2 Hoist Command-Level 2 Lamp Indication
C8110_SCW01_MO01 | EX1 | Dosing Screw Silo 1-Motor | [8 empty] | 1 | [14 empty] | NOT C8112_CN01_XGH | Tripped Breaker on VSD |  | Scale Comms
C8110_SCW02_MO01 | EX2 | Dosing Screw Silo 2-Motor | [8 empty] | 1 | [14 empty] | NOT C8112_CN01_XGH | Tripped Breaker on VSD |  | Scale Comms
C8110_SCW03_MO01 | EX3 | Dosing Screw Silo 3-Motor | [8 empty] | 1 | [14 empty] | NOT C8112_CN01_XGH | Tripped Breaker on VSD |  | Scale Comms
C8110_SCW04_MO01 | EX4 | Dosing Screw Silo 4-Motor | [8 empty] | 1 | [14 empty] | NOT C8112_CN01_XGH | Tripped Breaker on VSD |  | Scale Comms
C8110_SCW05_MO01 | EX5 | Dosing Screw Silo 5-Motor | [8 empty] | 1 | [14 empty] | NOT C8112_CN01_XGH | Tripped Breaker on VSD |  | Scale Comms
C8110_SCW06_MO01 | EX6 | Dosing Screw Silo 6-Motor | [8 empty] | 1 | [14 empty] | NOT C8112_CN01_XGH | Tripped Breaker on VSD |  | Scale Comms
C8110_SCW07_MO01 | EX7 | Dosing Screw Silo 7-Motor | [8 empty] | 1 | [14 empty] | NOT C8112_CN01_XGH | Tripped Breaker on VSD |  | Scale Comms
C8110_SCW08_MO01 | EX8 | Dosing Screw Silo 8-Motor | [8 empty] | 1 | [14 empty] | NOT C8112_CN01_XGH | Tripped Breaker on VSD |  | Scale Comms
C8110_SCW09_MO01 | EX9 | Dosing Screw Silo 9-Motor | [8 empty] | 1 | [14 empty] | NOT C8112_CN01_XGH | Tripped Breaker on VSD |  | Scale Comms
C8110_VB09_MO01 | EX9 | Dosing Vibro Silo 9-Motor
C8110_VB09_MO02 | EX9 | Dosing Vibro Silo 9-Motor
C8110_SCW10_MO01 | EX10 | Dosing Screw Silo 10-Motor | [8 empty] | 1 | [14 empty] | NOT C8112_CN01_XGH | Tripped Breaker on VSD |  | Scale Comms
C8110_VB10_MO01 | EX10 | Dosing Vibro Silo 10-Motor
C8110_VB10_MO02 | EX10 | Dosing Vibro Silo 10-Motor
C8110_SCW13_MO01 | EX13 | Dosing Screw Silo 13-Motor | [8 empty] | 1 | [14 empty] | NOT C8112_CN01_XGH | Tripped Breaker on VSD |  | Scale Comms
C8110_SCW14_MO01 | EX14 | Dosing Screw Silo 14-Motor | [8 empty] | 1 | [14 empty] | NOT C8112_CN01_XGH | Tripped Breaker on VSD |  | Scale Comms
C8110_SCW15_MO01 | EX15 | Dosing Screw Silo 15-Motor | [8 empty] | 1 | [14 empty] | NOT C8112_CN01_XGH | Tripped Breaker on VSD |  | Scale Comms
C8110_SCW16_MO01 | EX16 | Dosing Screw Silo 16-Motor | [8 empty] | 1 | [14 empty] | NOT C8112_CN01_XGH | Tripped Breaker on VSD |  | Scale Comms
C8110_VB16_MO01 | EX16 | Dosing Vibro Silo 16-Motor
C8110_VB16_MO02 | EX16 | Dosing Vibro Silo 16-Motor
C8110_SCW17_MO01 | EX17 | Dosing Screw Silo 17-Motor | [8 empty] | 1 | [14 empty] | NOT C8112_CN01_XGH | Tripped Breaker on VSD |  | Scale Comms
C8110_SCW18_MO01 | EX18 | Dosing Screw Silo 18-Motor | [8 empty] | 1 | [14 empty] | NOT C8112_CN01_XGH | Tripped Breaker on VSD |  | Scale Comms
C8110_SCW19_MO01 | EX19 | Dosing Screw Silo 19-Motor | [8 empty] | 1 | [14 empty] | NOT C8112_CN01_XGH | Tripped Breaker on VSD |  | Scale Comms
C8110_VB19_MO01 | EX19 | Dosing Vibro Silo 19-Motor
C8110_VB19_MO02 | EX19 | Dosing Vibro Silo 19-Motor
C8110_SCW20_MO01 | EX20 | Dosing Screw Silo 20-Motor | [8 empty] | 1 | [14 empty] | NOT C8112_CN01_XGH | Tripped Breaker on VSD |  | Scale Comms
C8110_SCW23_MO01 | EX23 | Dosing Screw Silo 23-Motor | [8 empty] | 1 | [14 empty] | NOT C8112_CN01_XGH | Tripped Breaker on VSD |  | Scale Comms
C8110_SCW24_MO01 | EX24 | Dosing Screw Silo 24-Motor | [8 empty] | 1 | [14 empty] | NOT C8112_CN01_XGH | Tripped Breaker on VSD |  | Scale Comms
C8110_SCW25_MO01 | EX25 | Dosing Screw Silo 25-Motor | [8 empty] | 1 | [14 empty] | NOT C8112_CN01_XGH | Tripped Breaker on VSD |  | Scale Comms
C8112_CN01_MO01 | T09 | Primary Dosing Scale Discharge Conveyor-Motor |  | 1 | [21 empty] | C8114_CN01_MO01
C8112_FA01_MO01 | FT09 | Scale Discharge Conveyor Aspiration Fan-Motor
C8114_CN01_MO01 | T10 | Batch Transport Conveyor 1-Motor |  | 1 | [21 empty] | C8114_EV01_MO01
C8114_FA01_MO01 | FT10 | Batch Transport Conveyor Aspiration Fan-Motor
C8114_EV01_MO01 | E03 | Batch Transport Elevator 1-Start | 1 |  | 1 | [19 empty] | 4 MGs
C8114_FA02_MO01 | FE3 | Batch Transport Elevator Aspiration Fan-Motor
C8120_MX01_MO01 | M02 | Pre-Mixer-Motor
C8122_SCW01_MO01 | AL01 | Grinder 1 Feed Screw-Motor |  | 1 |  |  |  |  | 1 |  |  |  |  | 1 | [11 empty] | C8122_CR01_MO01 |  | From VSD
C8122_SCW01_MO02 | AL01 | Grinder 1 Feed Screw-Forced Ventilation Motor | [11 empty] | 1
C8122_CR01_MO01 | PB01 | Grinder 1 Lump Crusher-Motor |  |  | 1 |  |  |  | 1 |  | 1 |  |  | 1 | [10 empty] | 2 TTs and 2 MCBs | C8122_ML01_MO01 | Soft Starter Fault
C8122_ML01_MO01 | BR01 | Grinder 1-Motor | [6 empty] | 1 | 1 | 1 | 1 |  | 1 | [10 empty] | 2 TTs and 2 MCBs | C8124_SCW01_MO01
C8122_ML01_SS02_LP01 | KA180 | Grinder 1 Door Safety System-Indication Lamp
C8122_FA01_MO01 | VE03 | Grinder 1 Extract Fan-Motor | [8 empty] | 1 |  |  | 1 | [12 empty] | VSD Fault
C8122_SCW02_MO01 | AL02 | Grinder 2 Feed Screw-Motor |  | 1 |  |  |  |  | 1 |  |  |  |  | 1 | [11 empty] | C8122_CR02_MO01 |  | From VSD
C8122_SCW02_MO02 | AL02 | Grinder 1 Feed Screw-Forced Ventilation Motor | [11 empty] | 1
C8122_CR02_MO01 | PB02 | Grinder 2 Lump Crusher-Motor |  |  | 1 |  |  |  | 1 |  | 1 |  |  | 1 | [10 empty] | 2 TTs and 2 MCBs | C8122_ML02_MO01 | Soft Starter Fault
C8122_ML02_MO01 | BR02 | Grinder 2-Motor | [6 empty] | 1 | 1 | 1 | 1 |  | 1 | [10 empty] | 2 TTs and 2 MCBs | C8124_SCW02_MO01
C8122_ML02_SS02_LP01 | KA180 | Grinder 2 Door Safety System-Indication Lamp
C8122_FA02_MO01 | VE04 | Grinder 2 Extract Fan-Motor | [8 empty] | 1 |  |  | 1 | [12 empty] | VSD Fault
C8124_RV01_MO01 | EC02 | Grinder 1 Rotary Valve-Motor
C8124_SCW01_MO01 | T13 | Grinder 1 Discharge Screw-Motor |  | 1 | [21 empty] | C8124_SCW01_MO01
C8124_RV02_MO01 | EC03 | Grinder 2 Rotary Valve-Motor
C8124_SCW02_MO01 | T14 | Grinder 2 Discharge Screw-Motor |  | 1 | [21 empty] | C8124_RV02_MO01
C8130_FA01_MO01 | VE07 | Weigh Bin Extract Fan-Motor
C8130_SCW31_MO01 | EX7 | Dosing Screw Silo 31-Motor | [8 empty] | 1 | [14 empty] | NOT C8114_CN01_XGH | Tripped Breaker on VSD |  | Scale Comms
C8130_SCW32_MO01 | EX8 | Dosing Screw Silo 32-Motor | [8 empty] | 1 | [14 empty] | NOT C8114_CN01_XGH | Tripped Breaker on VSD |  | Scale Comms
C8130_SCW33_MO01 | EX9 | Dosing Screw Silo 33-Motor | [8 empty] | 1 | [14 empty] | NOT C8114_CN01_XGH | Tripped Breaker on VSD |  | Scale Comms
C8130_SCW34_MO01 | EX10 | Dosing Screw Silo 34-Motor | [8 empty] | 1 | [14 empty] | NOT C8114_CN01_XGH | Tripped Breaker on VSD |  | Scale Comms
C8140_SB55_MO01 | DE55 | Scraper Bottom Silo 55-Motor | [10 empty] | 1 | 1
C8140_SCW55_MO01 | EX55 | Dosing Screw Silo 55-Motor | [8 empty] | 1 |  | 1 | [12 empty] | C8140_FV55_FB02 | Tripped Breaker on VSD |  | Scale Comms
C8140_SB56_MO01 | DE56 | Scraper Bottom Silo 56-Motor | [10 empty] | 1 | 1
C8140_SCW56_MO01 | EX56 | Dosing Screw Silo 56-Motor | [8 empty] | 1 |  | 1 | [12 empty] | C8140_FV56_FB02 | Tripped Breaker on VSD |  | Scale Comms
C8140_SB57_MO01 | DE57 | Scraper Bottom Silo 57-Motor | [10 empty] | 1 | 1
C8140_SCW57_MO01 | EX57 | Dosing Screw Silo 57-Motor | [8 empty] | 1 |  | 1 | [12 empty] | C8140_FV57_FB02 | Tripped Breaker on VSD |  | Scale Comms
C8140_SB58_MO01 | DE58 | Scraper Bottom Silo 58-Motor | [10 empty] | 1 | 1
C8140_SCW58_MO01 | EX58 | Dosing Screw Silo 58-Motor | [8 empty] | 1 |  | 1 | [12 empty] | C8140_FV58_FB02 | Tripped Breaker on VSD |  | Scale Comms
C8140_SB59_MO01 | DE59 | Scraper Bottom Silo 59-Motor | [10 empty] | 1 | 1
C8140_SCW59_MO01 | EX59 | Dosing Screw Silo 59-Motor | [8 empty] | 1 |  | 1 | [12 empty] | C8140_FV59_FB02 | Tripped Breaker on VSD |  | Scale Comms
C8140_SB60_MO01 | DE60 | Scraper Bottom Silo 60-Motor | [10 empty] | 1 | 1
C8140_SCW60_MO01 | EX60 | Dosing Screw Silo 60-Motor | [8 empty] | 1 |  | 1 | [12 empty] | C8140_FV60_FB02 | Tripped Breaker on VSD |  | Scale Comms
C8140_SCW61_MO01 | EX61 | Dosing Screw Silo 61-Motor | [8 empty] | 1 |  | 1 | [12 empty] | C8140_FV61_FB02 | Tripped Breaker on VSD |  | Scale Comms
C8140_SCW62_MO01 | EX62 | Dosing Screw Silo 62-Motor | [8 empty] | 1 |  | 1 | [12 empty] | C8140_FV62_FB02 | Tripped Breaker on VSD |  | Scale Comms
C8140_SCW63_MO01 | EX63 | Dosing Screw Silo 63-Motor | [8 empty] | 1 |  | 1 | [12 empty] | C8140_FV63_FB02 | Tripped Breaker on VSD |  | Scale Comms
C8140_SCW64_MO01 | EX64 | Dosing Screw Silo 64-Motor | [8 empty] | 1 |  | 1 | [12 empty] | C8140_FV64_FB02 | Tripped Breaker on VSD |  | Scale Comms
C8140_SCW65_MO01 | EX65 | Dosing Screw Silo 65-Motor | [8 empty] | 1 |  | 1 | [12 empty] | C8140_FV65_FB02 | Tripped Breaker on VSD |  | Scale Comms
C8140_SCW66_MO01 | EX66 | Dosing Screw Silo 66-Motor | [8 empty] | 1 |  | 1 | [12 empty] | C8140_FV66_FB02 | Tripped Breaker on VSD |  | Scale Comms
C8140_SCW67_MO01 | EX67 | Dosing Screw Silo 67-Motor | [8 empty] | 1 |  | 1 | [12 empty] | C8140_FV67_FB02 | Tripped Breaker on VSD |  | Scale Comms
C8140_SCW68_MO01 | EX68 | Dosing Screw Silo 68-Motor | [8 empty] | 1 |  | 1 | [12 empty] | C8140_FV68_FB02 | Tripped Breaker on VSD |  | Scale Comms
C8142_HM01_SV02 |  | Hammer on Micro Scale 1-Solenoid Valve
C8142_MX01_MO01 | M08 | Micro Mixer-Motor | [10 empty] | 1 | 1
C8150_FA01_MO01 | VS02 | Main Mixer Aspiration Fan-Motor
C8150_FI01_SV02 | FI25 | Main Mixer Filter-Solenoid Valve
C8150_MX01_MO01 | M03 | Main Mixer-Motor | [6 empty] | 1 | [5 empty] | 1
C8150_CN01_MO01 | T15 | Main Mixer Conveyor-Motor |  | 1 | [21 empty] | C8152_EV01_MO01
C8152_EV01_MO01 | E05 | Mixer Elevator-Start | 1 |  | 1 | [19 empty] | 4 MGs
C8152_FA01_MO01 | FE5 | Mixer Elevator Aspiration Fan-Motor
C8152_DB01_MO01 | DI04 | Distributor - Extruder Pre-Bins-Motor
C8210_FA01_MO01 | FI51 | Exturder Pre-Bin 1 Aspiration Fan-Motor
C8210_FI01_SV02 | FI51 | Exturder Pre-Bin 1 Filter-Solenoid Valve
C8210_FA02_MO01 | FI52 | Exturder Pre-Bin 2 Aspiration Fan-Motor
C8210_FI02_SV02 | FI52 | Exturder Pre-Bin 2 Filter-Solenoid Valve
C8210_SCW01_MO01 | EX41 | Discharge Screw Extruder Pre-Bin 1-Motor |  | 1 | [6 empty] | 1 | [14 empty] | C8210_SCW05_MO01 | Tripped Breaker on VSD
C8210_SCW02_MO01 | EX42 | Discharge Screw Extruder Pre-Bin 2-Motor |  | 1 | [6 empty] | 1 | [14 empty] | C8210_SCW05_MO01 | Tripped Breaker on VSD
C8210_SCW05_MO01 | T08 | Discharge Screw Extruder Pre-Bins-Motor |  | 1 | [21 empty] | C8210_SI01_MO01 OR C8210_SI02_MO01
C8210_SI01_MO01 | TA14 | Exturder Sifter 1-Motor | [23 empty] | C8210_SCW06_MO01
C8210_SI02_MO01 | TA15 | Exturder Sifter 2-Motor | [23 empty] | C8210_SCW06_MO01
C8210_SCW06_MO01 | T22 | Sifter Discharge Screw Extruder-Motor |  | 1 | [24 empty] | Magnet Door Open
C8210_FA05_MO01 | VE29 | Loss-in-Weight Buffer Tank Fan-Motor
C8210_CN01_MO01 | T26 | Conveyor to LIW-Motor |  | 1 | [24 empty] | Scale Comms
C8210_FA06_MO01 | VE30 | Aspiration Fan LIW Conveyor-Motor
C8210_FA07_MO01 | VE31 | Aspiration Fan LIW Tank-Motor
C8210_LIW01_DO01 | TR07 | Loss-in-Weight System-Jesma Controller
C8210_LIW01_DO02 | TR07 | Loss-in-Weight System-Jesma Controller
C8210_SB01_MO01 | VF01 | LIW Tank Scarper Bottom-Motor
C8210_SCW07_MO01 | T27 | LIW Feed Screw-MOTOR | [6 empty] | 1 |  |  |  |  | 1 | [11 empty] | C8220_MX01_MO01 AND C8210_BV01_FB02
C8220_MX01_MO01 | COND01 | Pre-Conditioner 1-Motor |  |  | 1 |  |  |  |  | 1 | [15 empty] | C8220_MX02_MO01
C8220_MX02_MO01 | COND02 | Pre-Conditioner 2-Motor | [8 empty] | 1
C8220_EXT01_MO01 | M04 | Extruder-Motor |  |  | 1 |  |  |  | 1 |  | 1 | 1 |  | 1 |  |  | 1 | 1 | 1 | [5 empty] | 2 Safety Systems | C8220_EXT01_MO01 IF C8220_DV01_FB02 | VSD Fault |  | Brush Fault | Motor Housing Open | Torque Limiter
C8220_FA01_MO01 | VE72 | Extruder Forced Ventilation-Motor | [6 empty] | 1 |  |  |  |  | 1 |  |  | 1 | [11 empty] | Pressure Switch
C8220_FA02_MO01 |  | Extruder Motor VSD Ventilation-Motor | [11 empty] | 1
C8220_HE01_DO01 | R02 | Extruder Heating-Elements
C8220_HY01_PU01_MO01 | M17 | Extruder Hydraulic Pump-Motor | [11 empty] | 1
C8220_PU01_MO01 | M02 | Extruder Lubrication Pump-Motor | [6 empty] | 1 |  |  |  |  | 1 |  |  | 1 | 1 | [6 empty] | 2 TTs |  |  |  | Pressure Switch | Oil Filter Fault
C8220_PU02_MO01 | M12 | Extruder Lubrication Pump Reduced-Motor | [11 empty] | 1 |  |  | 1 | [11 empty] | Pressure Switch
C8220_DZ01_MO01 | DEG | Degasser-Motor | [8 empty] | 1 | [15 empty] | VSD Fault
C8220_CU01_MO01 | GRA01 | Extruder Cutter-Motor | [7 empty] | 1 | 1 | 1 |  | 1 | [12 empty] | VSD Fault
C8224_FA01_MO01 | VE23 | Extruder Flash-Off Fan-Motor
C8224_RV01_MO01 | EC23 | Extruder Flash-Off Rotary Valve-Motor
C8226_CN01_MO01 | T51 | Extruder Conveyor-Motor | [23 empty] | C8228_EV01_MO01
C8228_EV01_MO01 | E18 | Extruder Elevator-Motor | [8 empty] | 1 | [14 empty] | Dryer OK
C8232_VB01_MO01 | AV01 | Vibro Conveyor after Dryer-Motor | [11 empty] | 1 | [11 empty] | C8232_EV01_MO01
C8232_VB01_MO02 | AV01 | Vibro Conveyor after Dryer-Motor | [11 empty] | 1 | [11 empty] | C8232_EV01_MO01
C8232_EV01_MO01 | E12 | Elevator after Dryer-Motor |  |  | 1 | [8 empty] | 1
C8232_FA01_MO01 | VE32 | Elevator Aspiration Fan-Motor | [11 empty] | 1
C8234_SI01_MO01 | TA09 | Coater Sifter-Motor | [11 empty] | 1 | [11 empty] | C8234_CN01_MO01
C8234_CN01_MO01 | T40 | Conveyor to Coater Pre-Bin-Motor |  |  | 1 | [8 empty] | 1
C8234_FA01_MO01 | VE70 | Vacuum Coater Aspiration Fan-Motor | [11 empty] | 1
C8234_SCW01_MO01 | T61 | Screw Conveyor to Waste-Motor | [11 empty] | 1 | [11 empty] | C8270_DE01_MO01
C8235_PU01_MO01 | PO11 | Fish Oil Dosing Pump-Motor | [8 empty] | 1 |  |  | 1 | [11 empty] | C8235_BV01_FB02 | VSD Fault
C8235_PU02_MO01 | PO47 | Veg Oil Dosing Pump-Motor | [8 empty] | 1 |  |  | 1 | [11 empty] | C8235_BV02_FB02
C8235_PU03_MO01 | PO38 | Oil Trimmings Dosing Pump-Motor | [8 empty] | 1 |  |  | 1 | [11 empty] | C8235_BV03_FB02
C8236_PU01_MO01 | PO49 | Coater Fat Sealant Pump-Motor | [8 empty] | 1 | [15 empty] | VSD Fault
C8236_PU02_MO01 | PO39 | Coater Biol Pump-Motor | [8 empty] | 1 | [14 empty] | C8236_BV09_FB02 | VSD Fault
C8236_VC01_MX01_MO01 | M07 | Vacuum Coater Mixer-Motor | [8 empty] | 1 |  | 1 | 1 | [12 empty] | VSD Fault
C8236_VP01_MO01 | PO41 | Vacuum Pump 1-Motor | [10 empty] | 1 | 1
C8236_VP02_MO01 | PO42 | Vacuum Pump 2-Motor | [10 empty] | 1 | 1
C8238_VB01_MO01 | AV02 | Coater Discharge Vibro-Motor | [8 empty] | 1 |  |  | 1 | [11 empty] | C8238_EV01_MO01 | Tripped Breaker for common supply
C8238_VB01_MO02 | AV02 | Coater Discharge Vibro-Motor | [8 empty] | 1 |  |  | 1 | [11 empty] | C8238_EV01_MO01 | Tripped Breaker for common supply
C8238_EV01_MO01 | E17 | Elevator after Coater-Motor |  |  | 1 | [8 empty] | 1
C8243_VB01_MO01 | AV03 | Cooler Discharge Vibro-Motor | [8 empty] | 1 |  |  | 1 | [11 empty] | C8243_EV01_MO01 | Tripped Breaker for common supply
C8243_VB01_MO02 | AV03 | Cooler Discharge Vibro-Motor | [8 empty] | 1 |  |  | 1 | [11 empty] | C8243_EV01_MO01 | Tripped Breaker for common supply
C8243_EV01_MO01 | E21 | Elevator after Cooler-Motor |  |  | 1 | [8 empty] | 1 | [11 empty] | C8243_EV02_MO01
C8243_EV02_MO01 | E42 | Elevator to MVS-Motor |  |  | 1 | [8 empty] | 1 |  |  | 1 | [11 empty] | Pressure Switch
C8250_DV01_LP01 | BD05 | Diverter After MVS-Lamp
C8250_DV01_LP02 | BD05 | Diverter After MVS-Lamp
C8250_VB01_MO01 | AV04 | Packing Vibro Feeder-Motor 1 | [8 empty] | 1 |  |  | 1 | [10 empty] | 2 PFs | C8250_SI01_MO01 AND C8250_VB01_MO02 | Tripped Breaker for common supply AND Power On Signal
C8250_VB01_MO02 | AV04 | Packing Vibro Feeder-Motor 2 | [8 empty] | 1 |  |  | 1 | [10 empty] | 2 PFs | C8250_SI01_MO01 AND C8250_VB01_MO02 | Tripped Breaker for common supply AND Power On Signal
C8250_SI01_MO01 | TA03 | Finished Product Sifter-Motor Left | [10 empty] | 1 | 1 | [12 empty] | Pressure Switch
C8250_SI01_MO02 | TA03 | Finished Product Sifter-Motor Right | [10 empty] | 1 | 1 | [12 empty] | Pressure Switch
C8251_EV01_MO01 | E08 | Elevator after MVS-Motor |  | 1 | 1 | [8 empty] | 1
C8251_DB01_MO01 | DI07 | Semi-Finished Product Distributor-Start | [11 empty] | 1
C8252_CN01_MO01 | T20 | Conveyor to Packing Lines-Motor |  | 1
C8252_EV01_MO01 | E22 | Elevator from Packing Silos-Start |  |  | 1 |  |  |  |  | 1 |  |  |  | 1
C8259_MVS01_MO01 |  | MVS Sprayer-Motor |  |  | 1
C8259_MVS02_MO01 |  | MVS Spray Cylinder-Motor |  |  | 1
C8259_BL01_MO01 |  | MVS Blower-Motor | [11 empty] | 1
C8259_PU01_MO01 | 1DP1 | MVS Dosing Pump-Motor | [23 empty] | Valve Open (C8259_BV02 OR BV03. If BV03 then also BV04 OR BV05)
C8259_PU02_MO01 | 7VP1 | MVS Cold Oil Pump-Motor | [23 empty] | C8259_BV07_FB02
C8259_PU03_MO01 | PO06 | MVS Oil Refill Pump-Motor | [11 empty] | 1 | [11 empty] | C8259_BV09_FB02
C8259_PU04_MO01 | 15EPV5 | MVS Enzyme Dosing Pump-Motor
C8259_PU05_MO01 |  | MVS Enzyme Dosing Pump-Motor | [23 empty] | C8259_BV10_FB02
C8259_CH01_DO01 |  | MVS Cooling System-Chillers
C8259_SCW01_MO01 |  | MVS Solid Feeder-Motor
C8260_CN01_MO01 | T28 | Conveyor to Big Bag Packing-Start |  | 1 | [8 empty] | 1 | 1
C8260_LF01_MO01 |  | Hoist for Big Bags-Start | [10 empty] | 1 | 1
C8260_FA01_MO01 | VE02 | Extract Fan - Big Bag-Start | [10 empty] | 1 | 1
C8260_BE01_MO01 | T29 | Conveyor after Big Bag Weighing-
C8270_DE01_MO01 | EX50 | Fines Recovery Disc Elevator-Motor |  |  | 1 | [23 empty] | Chainguard
C8270_SCW01_MO01 | EX45 | Rework Dosing Screw-Motor | [26 empty] | Scale Comms
C8822_CN01_MO01 | T19 | Conveyor to Crumbler-Start |  | 1 | [9 empty] | 1
C8822_SCW01_MO01 | CY03 | Feed Screw-Crumbler | [11 empty] | 1 | [11 empty] | C8822_CM01_MO01
C8822_CM01_MO01 | CY03 | Pellet Crumbler-Crumbler | [11 empty] | 1 | [11 empty] | C8828_SI01_MO01
C8822_CM01_MO02 | CY03 | Pellet Crumbler-Gap Adjustment Right | [11 empty] | 1
C8822_CM01_MO03 | CY03 | Pellet Crumbler-Gap Adjustment Left | [11 empty] | 1
C8828_SI01_MO01 | TA21 | Sifter After Crumbler- | [11 empty] | 1
C8828_DE01_MO01 | T76 | Disc Elevator Crumbling- | [11 empty] | 1
C8828_SCW01_MO01 | T77 | Screw Conveyor 1 Crumbling- | [11 empty] | 1 | [11 empty] | C8828_SI02_MO01
C8828_SI02_MO01 | TA22 | Final Sifter- | [11 empty] | 1
C8828_FA01_MO01 | EC40 | Aspiration Fan- | [11 empty] | 1
C8828_FI01_MO01 | FI40 | Bagging Filter- | [26 empty] | Blocked
C8833_RV01_MO01 | APIA | Rotary Valve-Motor | [11 empty] | 1
C8833_SCW01_MO01 | APIA | Transport Screw-Motor | [11 empty] | 1
C8835_TA01_MX01_MO01 | - | Liquid Tank Mixer-Crumbler | [11 empty] | 1
C8835_PU01_MO01 | - | Pump-Crumbler | [11 empty] | 1
C8836_MX01_MO01 | M06 | Micro Addition Mixer-Crumbler | [7 empty] | 1 |  | 1 |  | 1
C8838_VB01_MO01 | AV21 | Vibro Feeder to Bucket Packer-Motor | [11 empty] | 1 | [11 empty] | C8838_EV01_MO01
C8838_EV01_MO01 | E74 | Elevator to Bucket Packer-Motor | [11 empty] | 1
C3301_PU01_MO01 | PO26 | Process Water Pump PreCon-Motor | [8 empty] | 1 | [14 empty] | C3601_BV01_FB02 | VSD Fault
C3301_PU02_MO01 | PO13 | Process Water Pump Extruder-Motor | [8 empty] | 1
C3801_PU01_MO01 | PO01 | Oil Pump to Day Tank 3-Motor | [23 empty] | C3801_BV01_FB02
C3801_PU02_MO01 | PO02 | Oil Pump to Day Tank 2-Motor | [23 empty] | C3801_BV02_FB02
C3801_PU03_MO01 | PO03 | Oil Pump to Day Tank 1-Motor | [23 empty] | C3801_BV03_FB02
C3802_TA01_MX01_MO01 | AG5.1 | Day Tank 1 Mixer-Motor | [11 empty] | 1
C3802_TA02_MX01_MO01 | AG02 | Day Tank 2 Mixer-Motor
C3802_TA03_MX01_MO01 | AG03 | Day Tank 3 Mixer-Motor
C3810_PU01_MO01 | PO13 | Oil Pump to Fat Sealant Buffer Tank-Motor | [8 empty] | 1 |  |  | 1 | [11 empty] | C3810_BV01_FB02 | VSD Fault
C3810_PU02_MO01 | PO46 | Fat Sealant Circulation Pump-Motor | [8 empty] | 1 | [15 empty] | VSD Fault
C3810_SO01_VB01 |  | Fat Sealant Flakes Silo-Vibro
C3810_EV01_MO01 |  | Fat Sealant Flakes Elevator-Motor
C3810_HE01_XX01 |  | Fat Sealant Heater-Stage 1
C3810_HE01_XX02 |  | Fat Sealant Heater-Stage 2
C3810_HE01_XX03 |  | Fat Sealant Heater-Stage 3
C3810_HE01_XX04 |  | Fat Sealant Heater-Stage 4
C3810_HE01_XX05 |  | Fat Sealant Heater-Stage 5
C3810_TA02_MX01_MO01 |  | Fat Sealant Tank Mixer-Motor | [8 empty] | 1 | [15 empty] | VSD Fault
C3810_TA02_HE01_XX01 |  | Fat Sealant Mixer Tank Heater-Stage 1
C3810_TA02_HE01_XX02 |  | Fat Sealant Mixer Tank Heater-Stage 2
C3820_PU01_MO01 | PO27 | Spare Oil Pump-Motor | [8 empty] | 1 | [15 empty] | VSD Fault
C3820_PU02_MO01 | PO48 | Oil Pump to Extruder-Motor
C3851_HE01_DO01 | L1.04 | Liquid Additive 1 Room Heater-Heating Controls
C3851_HE02_DO01 | L1.08 | Liquid Additive 1 Hose Heater-Heating Controls
C3851_HE03_DO01 | L1.13 | Liquid Additive 1 Pipe Heater-Heating Controls
C3851_PU01_MO01 | L1.02 | Liquid Additive 1 Pump-Motor | [23 empty] | C3820_BV03_FB02